## INDEX
CAM CALCULATION SHEET
INDEX
Area Summary
Area Breakup - Mall
Aarea Breakup- Office
Area Breakup- Common Area
Comm. Services
CAM Variables
CAM Charge Summary
CAM Charge Calculation Sheet
AMC Cost
Common Electrical Load
Electrical Load Breakup
HVAC Charges-Mall
AHU Load- Mall
Manpower Deplyment & Costing
Salary Breakup- Support Staff
Service Equipments Cost- HK, Security
Sinking Fund Calculation

## Area Summary
AREA STATEMENT |  |  |  |  | INDEX
BUILT-UP AREA STATEMENT
PLOT AREA = 8082.16 Sq.m
Actual areas
Sr No. | Description | Built Up Area | Leasable Area | Air conditioned Area
A | Parking/Services
1 | 2nd Basement | 70796.9808
2 | 3rd Basement | 70796.9808
3 | 4th Basement | 70796.9808
4 | 1st Basement (MEP) | 66168.8914 | 66168.8914
278559.8338
B | Mall
2 | Ground (Retail) | 35978.67 | 44426.5701
3 | L1(Retail) | 34642.8576 | 46313.4447
4 | L2(Retail) | 36523.3284 | 51865.3545
5 | L3(Food Court) | 48631.752 | 44518
| Total Mall Area | 155776.608 | 187123.3693 | 84205.5162
C | Office
1 | Office-L4 | 46058.0796 | 58033.1803
| Office-L5 | 44248.6512 | 55753.3005
| Office-L6 | 46058.0796 | 58033.1803
| Office-L7 | 46058.0796 | 58033.1803
| Office-L8 | 46058.0796 | 58033.1803
| Total Office Area | 182422.89 | 287886.0217 | 201520.2152
| TOTAL B+C+D |  | 475009.391

## Area-Mall
AREA STATEMENT
Sl. No. | Description | Carpet area |  | Built up area |  | Loading in % | Super BUA/Saleable area |  | efficiency | f/d
|  | Sq m | Sq ft | Sq m | Sq ft | % | Sq m | Sq ft | super / carpet
Ground Floor Area
1 | LG - 01 | 107.3 | 1154.9772 | 115.9 | 1247.5476 | 0.62 | 187.758 | 2021.0271 | 57.15% | 1.0801
2 | LG – 02 | 36.4 | 391.8096 | 40.3 | 433.7892 | 0.67 | 67.301 | 724.428 | 54.09% | 1.1071
3 | LG - 03 | 37.5 | 403.65 | 41.7 | 448.8588 | 0.67 | 69.639 | 749.5942 | 53.85% | 1.112
4 | LG – 04- Anchor 01 | 2244 | 24154.416 | 2285.9 | 24605.4276 | 0.24 | 2834.516 | 30510.7302 | 79.17% | 1.0187
5 | LG - 05 | 35.9 | 386.4276 | 39.2 | 421.9488 | 0.67 | 65.464 | 704.6545 | 54.84% | 1.0919
6 | LG - 06 | 61.8 | 665.2152 | 69 | 742.716 | 0.65 | 113.85 | 1225.4814 | 54.28% | 1.1165
7 | LG - 07 | 63.1 | 679.2084 | 70.2 | 755.6328 | 0.65 | 115.83 | 1246.7941 | 54.48% | 1.1125
8 | LG - 08 | 58.4 | 628.6176 | 63 | 678.132 | 0.65 | 103.95 | 1118.9178 | 56.18% | 1.0788
9 | LG - 09 | 20.8 | 223.8912 | 23.3 | 250.8012 | 0.67 | 38.911 | 418.838 | 53.46% | 1.1202
10 | LG - 10 | 58.7 | 631.8468 | 64.6 | 695.3544 | 0.65 | 106.59 | 1147.3348 | 55.07% | 1.1005
11 | LG - 11-1 | 252.5 | 2717.91 | 264.7 | 2849.2308 | 0.6 | 221.9435 | 2389 |  |  | Actual area sold (loading not done)
12 | LG - 11-2 | 252.5 | 2717.91 | 264.7 | 2849.2308 | 0.6 | 201.5766 | 2169.77 | 125.3% | 1.0483 | Actual area sold (loading not done)
| TOTAL |  |  |  | 35978.67 |  | 4127.3291 | 44426.5701
First Floor Area
1 | L1 - 01 | 146.4 | 1575.8496 | 155 | 1668.42 | 0.6 | 248 | 2669.472 | 59.03% | 1.0587
2 | L1 - 02 | 58.7 | 631.8468 | 63.6 | 684.5904 | 0.65 | 104.94 | 1129.5742 | 55.94% | 1.0835
3 | L1 - 03 | 28.8 | 310.0032 | 30.7 | 330.4548 | 0.67 | 51.269 | 551.8595 | 56.17% | 1.066
4 | L1 - 04-Anchor 01 | 2352 | 25316.928 | 2400 | 25833.6 | 0.24 | 2976 | 32033.664 | 79.03% | 1.0204
5 | L1 - 05 | 80.3 | 864.3492 | 84.5 | 909.558 | 0.65 | 139.425 | 1500.7707 | 57.59% | 1.0523
6 | L1 - 06 | 89.8 | 966.6072 | 96 | 1033.344 | 0.65 | 158.4 | 1705.0176 | 56.69% | 1.069
7 | L1 - 07 | 52.2 | 561.8808 | 56.6 | 609.2424 | 0.65 | 93.39 | 1005.25 | 55.89% | 1.0843
8 | L1 - 08 | 316.3 | 3404.6532 | 332 | 3573.648 | 0.6 | 531.2 | 5717.8368 | 59.54% | 1.0496
| TOTAL |  |  |  | 34642.8576 |  | 4302.624 | 46313.4447
Second Floor Area
1 | L2 - 01 | 66.2 | 712.5768 | 72.6 | 781.4664 | 0.65 | 119.79 | 1289.4196 | 55.26% | 1.0967
2 | L2 - 02 | 66.8 | 719.0352 | 72.3 | 778.2372 | 0.65 | 119.295 | 1284.0914 | 56% | 1.0823
3 | L2 - 03 | 33.3 | 358.4412 | 37 | 398.268 | 0.67 | 61.79 | 665.1076 | 53.89% | 1.1111
4 | L2 - 04- Anchor 01 | 1800.8 | 19383.8112 | 1832.6 | 19726.1064 | 0.28 | 2345.728 | 25249.4162 | 76.77% | 1.0177
5 | L2 - 05 (kiosk) | 16 | 172.224 | 19 | 204.516 | 0.67 | 31.73 | 341.5417 | 50.43% | 1.1875
6 | L2 - 06 | 96.7 | 1040.8788 | 102.6 | 1104.3864 | 0.65 | 169.29 | 1822.2376 | 57.12% | 1.061
7 | L2- 07 | 220.3 | 2371.3092 | 226.8 | 2441.2752 | 0.6 | 362.88 | 3906.0403 | 60.71% | 1.0295
8 | L2 - 08 | 61.3 | 659.8332 | 66.2 | 712.5768 | 0.65 | 109.23 | 1175.7517 | 56.12% | 1.0799
9 | L2 – 09 | 898.5 | 9671.454 | 926.7 | 9974.9988 | 0.55 | 1436.385 | 15461.2481 | 62.55% | 1.0314
10 | L2 – 10 (kiosk) | 34 | 365.976 | 37.3 | 401.4972 | 0.67 | 62.291 | 670.5003 | 54.58% | 1.0971
| TOTAL |  |  |  | 36523.3284 |  | 4818.409 | 51865.3545
Third Floor Area
1 | Edutainemnt Centre/ Restaurant- 01 | [6 empty] | 20148
2 | Restaurant - 02 | [6 empty] | 4693
3 | Restaurant - 03 | [6 empty] | 8219
4 | Restaurant - 04 | [6 empty] | 3923
5 | Restaurant - 05 | [6 empty] | 7535
[7 empty] | TOTAL | 44518
[5 empty] | Complete area/ SBU of mall |  |  | 187123.3693
|  |  | Complete area/ SBU of mall exculding LG and L1 achor stores |  |  |  |  | 124578.9751
|  |  | Total cam for mall exculding LG and L1 anchor stores. |  |  |  |  | 1868684.626
|  |  | Cam for LG L1 anchor stores |  |  |  |  | 296828.064
|  |  | Total CAM collection for mall |  |  |  |  | 2165512.69

## Area-Office
AREA STATEMENT- OFFICE
Sl. No. | Description | Carpet area |  | Built up area |  | Loading in % | Super BUA/Saleable area |  | efficiency | f/d
|  | Sq m | Sq ft | Sq m | Sq ft | % | Sq m | Sq ft | super / carpet
Fourth Floor
1 | OFFICE-01 | 1086.5 | 11695.086 | 1114.45 | 11995.9398 | 26% | 1404.207 | 15114.8841 | 79.37% | 1.0257
2 | OFFICE-02 | 718.45 | 7733.3958 | 739.95 | 7964.8218 | 26% | 932.337 | 10035.6755 | 79.37% | 1.0299
3 | OFFICE-03 | 518.1 | 5576.8284 | 530.3 | 5708.1492 | 26% | 668.178 | 7192.268 | 79.37% | 1.0235
4 | OFFICE-04 | 755 | 8126.82 | 778.3 | 8377.6212 | 26% | 980.658 | 10555.8027 | 79.37% | 1.0309
5 | OFFICE-05 | 589.35 | 6343.7634 | 604.5 | 6506.838 | 26% | 761.67 | 8198.6159 | 79.37% | 1.0257
6 | OFFICE-06 | 492.52 | 5301.4853 | 511.4 | 5504.7096 | 26% | 644.364 | 6935.9341 | 79.37% | 1.0383
| TOTAL |  |  |  | 46058.0796 |  | 5391.414 | 58033.1803
Fifth Floor
1 | OFFICE-01 | 1086.5 | 11695.086 | 1114.45 | 11995.9398 | 26% | 1404.207 | 15114.8841 | 79.37% | 1.0257
2 | OFFICE-02 | 706.45 | 7604.2278 | 735.45 | 7916.3838 | 26% | 926.667 | 9974.6436 | 79.37% | 1.0411 | Refuge area Reduction
3 | OFFICE-03 | 353.35 | 3803.4594 | 366.7 | 3947.1588 | 26% | 462.042 | 4973.4201 | 79.37% | 1.0378 | Refuge area Reduction
4 | OFFICE-04 | 755 | 8126.82 | 778.3 | 8377.6212 | 26% | 980.658 | 10555.8027 | 79.37% | 1.0309
5 | OFFICE-05 | 589.35 | 6343.7634 | 604.5 | 6506.838 | 26% | 761.67 | 8198.6159 | 79.37% | 1.0257
6 | OFFICE-06 | 492.52 | 5301.4853 | 511.4 | 5504.7096 | 26% | 644.364 | 6935.9341 | 79.37% | 1.0383
| TOTAL |  |  |  | 44248.6512 |  | 5179.608 | 55753.3005
Sixth Floor
1 | OFFICE-01 | 1086.5 | 11695.086 | 1114.45 | 11995.9398 | 26% | 1404.207 | 15114.8841 | 79.37% | 1.0257
2 | OFFICE-02 | 718.45 | 7733.3958 | 739.95 | 7964.8218 | 26% | 932.337 | 10035.6755 | 79.37% | 1.0299
3 | OFFICE-03-1 | 125.36 | 1349.375 | 128.3 | 1381.0212 | 26% | 161.658 | 1740.0867 | 79.37% | 1.0235
4 | OFFICE-03-2 | 392.74 | 4227.4534 | 402 | 4327.128 | 26% | 506.52 | 5452.1813 | 79.37% | 1.0236
5 | OFFICE-04 | 755 | 8126.82 | 778.3 | 8377.6212 | 26% | 980.658 | 10555.8027 | 79.37% | 1.0309
6 | OFFICE-05 | 589.35 | 6343.7634 | 604.5 | 6506.838 | 26% | 761.67 | 8198.6159 | 79.37% | 1.0257
7 | OFFICE-06 | 492.52 | 5301.4853 | 511.4 | 5504.7096 | 26% | 644.364 | 6935.9341 | 79.37% | 1.0383
| TOTAL |  |  |  | 46058.0796 |  | 5391.414 | 58033.1803
Seventh Floor
1 | OFFICE-01 | 1086.5 | 11695.086 | 1114.45 | 11995.9398 | 26% | 1404.207 | 15114.8841 | 79.37% | 1.0257
2 | OFFICE-02 | 718.45 | 7733.3958 | 739.95 | 7964.8218 | 26% | 932.337 | 10035.6755 | 79.37% | 1.0299
3 | OFFICE-03 | 518.1 | 5576.8284 | 530.3 | 5708.1492 | 26% | 668.178 | 7192.268 | 79.37% | 1.0235
4 | OFFICE-04 | 755 | 8126.82 | 778.3 | 8377.6212 | 26% | 980.658 | 10555.8027 | 79.37% | 1.0309
5 | OFFICE-05 | 589.35 | 6343.7634 | 604.5 | 6506.838 | 26% | 761.67 | 8198.6159 | 79.37% | 1.0257
6 | OFFICE-06 | 492.52 | 5301.4853 | 511.4 | 5504.7096 | 26% | 644.364 | 6935.9341 | 79.37% | 1.0383
| TOTAL |  |  |  | 46058.0796 |  | 5391.414 | 58033.1803
Eighth Floor
1 | OFFICE-01 | 1086.5 | 11695.086 | 1114.45 | 11995.9398 | 26% | 1404.207 | 15114.8841 | 79.37% | 1.0257
2 | OFFICE-02 | 718.45 | 7733.3958 | 739.95 | 7964.8218 | 26% | 932.337 | 10035.6755 | 79.37% | 1.0299
3 | OFFICE-03 | 518.1 | 5576.8284 | 530.3 | 5708.1492 | 26% | 668.178 | 7192.268 | 79.37% | 1.0235
4 | OFFICE-04 | 755 | 8126.82 | 778.3 | 8377.6212 | 26% | 980.658 | 10555.8027 | 79.37% | 1.0309
5 | OFFICE-05 | 589.35 | 6343.7634 | 604.5 | 6506.838 | 26% | 761.67 | 8198.6159 | 79.37% | 1.0257
6 | OFFICE-06 | 492.52 | 5301.4853 | 511.4 | 5504.7096 | 26% | 644.364 | 6935.9341 | 79.37% | 1.0383
| TOTAL |  |  |  | 46058.0796 |  | 5391.414 | 58033.1803
| Total | 20622.85 | 221984.3574 | 21226.4 | 228480.9696 | 26% Average | 26745.264 | 287886.0217

## Area-Comm
| AREA BREAKUP FOR COMMON AREA | [15 empty] | INDEX
| Common area components for each floor | B4 | B3 | B2 | B1 | LG | L1 | L2 | L3 | L4 | L5 | L6 | L7 | L8 | Total Sq Mtr | Total Sq ft
Non AC | Comm. Area | 745.8 | 451.17 | 451.7 | 2938 | 219.3 | 225.5 | 362.1 | 297.3 | 186.58 | 169.24 | 168.28 | 168.28 | 168.28 | 6551.53 | 70520.6689
Non AC | Common Toilet |  | 47 |  | 70 |  |  | 84.2 | 80.4 | [5 empty] | 281.6
Non AC | Services Area | 276.7 | 260.47 | 308 | 319 | 73.5 | 102 | 157 | 97 | 57.5 | 57.5 | 57.5 | 57.5 | 57.5 | 1881.17
Non AC | Service Yard |  |  |  | 554.6 | [9 empty] | 554.6
Non AC | Electrical (HT/LT/Transformer/Panel) |  |  |  | 619.1 | [9 empty] | 619.1
Non AC | DG |  |  |  | 264.4 | [9 empty] | 264.4
Non AC | Plumbing and Fire fighting |  |  |  | 197.3 | [9 empty] | 197.3
Non AC | Fire fighting and CCTV control |  |  |  | 48.4 | [9 empty] | 48.4
Non AC | STP | 325.4 | [12 empty] | 325.4
Non AC | WTP | [13 empty] | 0
Non AC | HVAC |  |  |  | 692.3 | [9 empty] | 692.3
Non AC | UPS and Battery |  |  |  | 31.7 | [9 empty] | 31.7
Non AC | ST-01 | 28.8 | 28.8 | 28.8 | 28.8 | 24 | 34.3 | 29.3 | 27 | 28.14 | 29.1 | 28.14 | 28.14 | 28.14 | 371.46
Non AC | ST-02 | [13 empty] | 0
Non AC | ST-03 | 29.5 | 29.5 | 29.5 | 27 | 61 | 28.4 | 29.2 | 29.2 | 44.8 | 26.5 | 26.5 | 26.5 | 26.5 | 414.1
Non AC | ST-04 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 33.3 | 25.74 | 25.74 | 25.74 | 25.74 | 25.74 | 374.8
Non AC | ST-05 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 32 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 396.8
Non AC | ST-06 | 24.6 | 24.6 | 24.6 | 24.6 | [9 empty] | 98.4
Non AC | Mall- Non AC | 45.8 | 45.8 | 45.8 | 56 | 56 | 56 | 56 | 33.6 | 0 | 0 | 0 | 0 | 0 | 395 | 4251.78
Non AC | Mall GE | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | [5 empty] | 134.4
Non AC | Mall SE | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | [5 empty] | 134.4
Non AC | Freight elevator | 12.2 | 12.2 | 12.2 | 22.4 | 22.4 | 22.4 | 22.4 | [6 empty] | 126.2
Non AC | Service lobby-Mall |  |  |  |  | 104.3 | 54.17 | 56.14 | 276.2 | [5 empty] | 490.81
| Common Toilet-Mall |  | 47 |  | 70 |  |  | 84.2 | 80.4 | [5 empty] | 281.6
AC | Mall- AC | 17 | 17 | 17 | 707.8 | 476 | 302 | 771.48 | 907.4 | 0 | 0 | 0 | 0 | 0 | 3215.68 | 34613.5795
AC | Mall BOH |  |  |  | 677.7 | [9 empty] | 677.7
AC | Mall lobby | 17 | 17 | 17 | 30.1 | [9 empty] | 81.1
AC | Corridor-Mall |  |  |  |  | 476 | 302 | 771.48 | 907.4 | [5 empty] | 2456.88
Non AC | Office | 34.8 | 34.8 | 34.8 | 80.1 | 34.8 | 34.8 | 34.8 | 34.8 | 64.3 | 215.3 | 64.3 | 64.3 | 64.3 | 603.4 | 6494.9976 |  | 8982.0198
Non AC | Office GE | 26.1 | 26.1 | 26.1 | 26.1 | 26.1 | 26.1 | 26.1 | 26.1 | 26.1 | 26.1 | 26.1 | 26.1 | 26.1 | 339.3
Non AC | Office SE | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 113.1
Non AC | Refuge Area | [9 empty] | 151 |  |  |  | 151
Non AC | Service lobby-Office |  |  |  | 45.3 |  |  |  |  | 29.5 | 29.5 | 29.5 | 29.5 | 29.5
AC | Office lobby | 24.35 | 24.35 | 24.35 | 42 | 116 | 0 | 0 | 0 | 228 | 271.8 | 228 | 228 | 228 | 231.05 | 2487.0222
AC | Office lobby | 24.35 | 24.35 | 24.35 | 42 | 116 | [8 empty] | 231.05
AC | Corridor-Office | [8 empty] | 228 | 271.8 | 228 | 228 | 228
[15 empty] | 10996.66 | 118368.0482

## Common Services
MAJOR COST HEADS FOR COMMON AREA CHARGES |  |  | INDEX
1 | Property Managenent Charges | Property Management Company Servcies Charges
Management Establishment Cost
2 | Engineering Services / Spares and Consumables / AMC | Engineering Manpower
Spares and Consumables
General Maintenance tools ( Amortized Cost)
AMC Charges
3 | Utility Cost ( Electricity , Air conditioning and Water) | Common Area Equipments / Lighting etc
Common Area Airconditioning Cost
Cost of water
5 | Janitorial / Gardening / Pest Control/ Security | Housekeeping Manpower
Housekeeping Equipments
Housekeeping Cleaning Consumables and Toiletries
Housekeeping Toiletries
Horticulture Manpower
Horticulture Tools and Consumables
Pest Control Services
Waste Management System
Façade Cleaning Services
Security Manpower Costing
6 | Liosaning, Licenses and Audit Cost | Electrical and DG License renewal
Lift License Renewal
Fire NOC
STP CTO
Labour license and registration
Liosaning & Licenses Cost
Environmental and Pollution Control Inspections
7 | Miscellaneous Costs | Rental Equipment (Pumps / Ladders etc)
Travel / Conveyance / Hire Charges Of taxi / cabs
Office Stationary and Printed Stationary
Site Team Communication Charges-Mobile
Mangzine, Journals and Newspapers
TV Cable Connection
Staff Welfare for deployed manpower ( CW & Sub Contractor)
Events and Festivel Expenses ( Decoration, Sweets, Consumables)
Courier Charges
Staff Uniforms
C&W administration cost for misc. expenses
8 | Audits | Energy Audit / Thermography and Harmonic Test
Financial Audit
Fire, Health & Safety Audits
Indoor Air Quality and DG emmission testing
Legal and professional servcies
Security Audit
Statutory compliances (PF, ESIC, Ptax, Lab.Welfare, Licenses, Returns, Audit etc.)
Water Testing Charges
9 | Insurance & Funds | Sinking Fund
Contigency Funds
Insurance Structural & Electro mechanical equipments
Group Accidential Insurance
Insurance for Thrid Party liability

## CAM Variables
CAM Variables-
Variable 1 |  |  |  | Mall Leasablke Area in sq ft | 187123.3693 | INDEX
|  |  |  | Office Space leasable area in sq ft | 287886.0217 |  | 475009.391
Variable 2 | Power Supply Details
|  | DG Set Supply |  | EB Supply
| Rates estimated for FY 14-15 | Rate | 64 | Fixed Charges ( KVA) | 350
|  | Unit per Ltrs. | 3.5 | Unit Rate ( KVAH) | 6.5
|  | Cost per Unit | 18.29 | Power Breakdown in hrs | 1.5
|  | Operation % | 6.25% | Operation % | 93.75%
Variable 3 | Minimum Wages Category |  |  | Basic | VDA
| Current Minimum wages rates |  | Skilled | 8079 | 1739
|  |  | Semiskilled | 6579 | 1419
|  |  | Unskilled | 5579 | 1199

## CAM Charges Summary
CAM CHARGE CALCULATION BASED ON BUILT UP AREA |  | 1st Year |  | 2nd Year |  | 3rd Year |  | INDEX
|  | Mall | Office | Mall | Office | Mall | Office
| AREA IN SQ. FT | CAM / sq ft | CAM / sq ft | CAM / sq ft | CAM / sq ft | CAM / sq ft | CAM / sq ft
| CAM COST PER MONTH PER SQ FT IN INR | 13.3222 | 9.9673 | 14.7233 | 11.7732 | 16.8349 | 13.2851
1 | Manpower Cost | 7.5386 | 5.2126 | 8.2925 | 5.7338 | 9.1217 | 6.3072
2 | Spares and Consumables ( Engineering & Building Services) | 0.89448 | 0.75264 | 0.95074 | 0.8018 | 0.98749 | 0.8311
3 | AMC Charges | 0 | 0 | 0.26962 | 0.90644 | 1.1752 | 1.5159
4 | Electricity Cost ( Utility & Common Area HVAC) | 1.6797 | 1.2593 | 1.7637 | 1.3223 | 1.8519 | 1.3884
5 | Audits | 0.091226 | 0.091226 | 0.12807 | 0.12807 | 0.12807 | 0.12807
6 | Liosaning & Licenses Cost | 0.07977 | 0.07977 | 0.078718 | 0.078718 | 0.078718 | 0.12807
7 | Administrative Expenses | 0.148 | 0.148 | 0.16484 | 0.16484 | 0.16484 | 0.16484
8 | Insurance, Sinking Fund | 1.4569 | 1.4569 | 1.5032 | 1.5032 | 1.5513 | 1.5513
9 | Profit Margin 10% on Actual Expense | 1.4335 | 0.96684 | 1.572 | 1.1341 | 1.7756 | 1.2702

## CAM Charges
PROPOSED CAM CHARGES
CAM CHARGE CALCULATION BASED ON BUILT UP AREA OF |  | 1st Year | [7 empty] | 2nd Year | [7 empty] | 3rd Year | [7 empty] | INDEX
|  | Combined Services |  | Mall |  |  | Office Area |  |  | Combined Services |  | Mall |  |  | Office Area |  |  | Combined Services |  | Mall |  |  | Office Area
| AREA IN SQ. FT | Area sft | 475009.391 | Area sft | 187123.3693 | CAM rate | Area sft | 287886.0217 | CAM rate | Area sft | 475009.391 | Area sft | 187123.3693 | CAM rate | Area sft | 287886.0217 | CAM rate | Area sft | 475009.391 | Area sft | 187123.3693 | CAM rate | Area sft | 287886.0217 | CAM rate
| CAM COST PER MONTH IN INR | Monthly Cost | 3888670.2694 | Monthly Cost | 1418705.6898 | 13.3222 | Monthly Cost | 704956.6982 | 9.9673 | Monthly Cost | 4357603.2893 | Monthly Cost | 1519040.5148 | 14.7233 | Monthly Cost | 950272.0895 | 11.7732 | Monthly Cost | 4976847.4297 | Monthly Cost | 1694248.7017 | 16.8349 | Monthly Cost | 1006110.0061 | 13.2358
CAM Charges INR/ Per sq ft / month |  | per sq. ft cost | 8.1903 | per sq. ft cost | 5.1357 |  | per sq. ft cost | 1.7808 |  | per sq. ft cost | 9.1676 | per sq. ft cost | 5.5496 |  | per sq. ft cost | 2.5995 |  | per sq. ft cost | 10.4731 | per sq. ft cost | 6.3575 |  | per sq. ft cost | 2.7584
1 | Manpower Cost | 2224001.7833 | 4.682 | 534537.1 | 2.8566 | 7.5386 | 152743.45 | 0.53057 | 5.2126 | 2446401.9617 | 5.1502 | 587990.81 | 3.1423 | 8.2925 | 168017.795 | 0.58363 | 5.7338 | 2691042.1578 | 5.6652 | 646789.891 | 3.4565 | 9.1217 | 184819.5745 | 0.64199 | 6.3072
a | Manpower Cost | 180000 | 0.37894 | 0 | 0 | 0.37894 |  | 0 | 0.37894 | 198000 | 0.41683 | 0 | 0 | 0.41683 | 0 | 0 | 0.41683 | 217800 | 0.45852 | 0 | 0 | 0.45852 | 0 | 0 | 0.45852
b | Management Staff | 495833.3333 | 1.0438 | 0 | 0 | 1.0438 | 0 | 0 | 1.0438 | 545416.6667 | 1.1482 | 0 | 0 | 1.1482 | 0 | 0 | 1.1482 | 599958.3333 | 1.263 | 0 | 0 | 1.263 | 0 | 0 | 1.263
c | Property Management Fee- IPC | 225000 | 0.47367 | 0 | 0 | 0.47367 | 0 | 0 | 0.47367 | 247500 | 0.52104 | 0 | 0 | 0.52104 | 0 | 0 | 0.52104 | 272250 | 0.57315 | 0 | 0 | 0.57315 | 0 | 0 | 0.57315
d | Engineering Manpower | 572810 | 1.2059 | 0 | 0 | 1.2059 | 0 | 0 | 1.2059 | 630091 | 1.3265 | 0 | 0 | 1.3265 | 0 | 0 | 1.3265 | 693100.1 | 1.4591 | 0 | 0 | 1.4591 | 0 | 0 | 1.4591
e | Custodial Services Manpower | 132704.45 | 0.27937 | 303957.1 | 1.6244 | 1.9037 | 95098.45 | 0.33033 | 0.60971 | 145974.895 | 0.30731 | 334352.81 | 1.7868 | 2.0941 | 104608.295 | 0.36337 | 0.67068 | 160572.3845 | 0.33804 | 367788.091 | 1.9655 | 2.3035 | 115069.1245 | 0.3997 | 0.73774
f | Horticulture Manpower | 45648 | 0.096099 | 0 | 0 | 0.096099 | 0 | 0 | 0.096099 | 50212.8 | 0.10571 | 0 | 0 | 0.10571 | 0 | 0 | 0.10571 | 55234.08 | 0.11628 | 0 | 0 | 0.11628 | 0 | 0 | 0.11628
g | Pest Control Services | 20000 | 0.042104 | 0 | 0 | 0.042104 | 0 | 0 | 0.042104 | 22000 | 0.046315 | 0 | 0 | 0.046315 | 0 | 0 | 0.046315 | 24200 | 0.050946 | 0 | 0 | 0.050946 | 0 | 0 | 0.050946
h | Façade Cleaning Services | 84952 | 0.17884 |  | 0 | 0.17884 |  | 0 | 0.17884 | 93447.2 | 0.19673 |  | 0 | 0.19673 |  | 0 | 0.19673 | 102791.92 | 0.2164 |  | 0 | 0.2164 |  | 0 | 0.2164
i | Security Services-manpower | 467054 | 0.98325 | 230580 | 1.2322 | 2.2155 | 57645 | 0.20024 | 1.1835 | 513759.4 | 1.0816 | 253638 | 1.3555 | 2.437 | 63409.5 | 0.22026 | 1.3018 | 565135.34 | 1.1897 | 279001.8 | 1.491 | 2.6807 | 69750.45 | 0.24228 | 1.432
2 | Spares and Consumables ( Engineering & Building Services) | 324620.2 | 0.6834 | 100268.2123 | 0.21109 | 0.89448 | 32889.2119 | 0.069239 | 0.75264 | 346329.72 | 0.7291 | 105281.6229 | 0.22164 | 0.95074 | 34533.6725 | 0.072701 | 0.8018 | 358519.956 | 0.75476 | 110545.7041 | 0.23272 | 0.98749 | 36260.3561 | 0.076336 | 0.8311
a | Engineering Spares and Consumables | 212095.2 | 0.44651 | 80768.2123 | 0.17003 | 0.61654 | 23389.2119 | 0.049239 | 0.49575 | 233304.72 | 0.49116 | 84806.6229 | 0.17854 | 0.66969 | 24558.6725 | 0.051701 | 0.54286 | 244969.956 | 0.51572 | 89046.9541 | 0.18746 | 0.70318 | 25786.6061 | 0.054287 | 0.57
b | Housekeeping Equipments | 30525 | 0.064262 |  | 0 | 0.064262 |  | 0 | 0.064262 | 30525 | 0.064262 | 0 | 0 | 0.064262 | 0 | 0 | 0.064262 | 30525 | 0.064262 | 0 | 0 | 0.064262 | 0 | 0 | 0.064262
c | Housekeeping Consumables and Toiletries | 10000 | 0.021052 | 19500 | 0.041052 | 0.062104 | 9500 | 0.02 | 0.041052 | 10500 | 0.022105 | 20475 | 0.043104 | 0.065209 | 9975 | 0.021 | 0.043104 | 11025 | 0.02321 | 21498.75 | 0.04526 | 0.06847 | 10473.75 | 0.02205 | 0.04526
f | Horticulture Tools and Consumables | 29000 | 0.061051 |  | 0 | 0.061051 |  | 0 | 0.061051 | 29000 | 0.061051 | 0 | 0 | 0.061051 | 0 | 0 | 0.061051 | 29000 | 0.061051 | 0 | 0 | 0.061051 | 0 | 0 | 0.061051
g | Security Equipments | 43000 | 0.090525 |  | 0 | 0.090525 |  | 0 | 0.090525 | 43000 | 0.090525 | 0 | 0 | 0.090525 | 0 | 0 | 0.090525 | 43000 | 0.090525 | 0 | 0 | 0.090525 | 0 | 0 | 0.090525
3 | AMC Charges | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128070 | 0.26962 | 0 | 0 | 0.26962 | 183333.3333 | 0.63683 | 0.90644 | 403829.3444 | 0.85015 | 60833.3333 | 0.3251 | 1.1752 | 191666.6667 | 0.66577 | 1.5159
4 | Electricity Cost ( Utility & Common Area HVAC) | 142946.1463 | 0.30093 | 654927.133 | 1.3788 | 1.6797 | 455237.0638 | 0.95837 | 1.2593 | 150093.4536 | 0.31598 | 687673.4896 | 1.4477 | 1.7637 | 477998.9169 | 1.0063 | 1.3223 | 157598.1263 | 0.33178 | 722057.1641 | 1.5201 | 1.8519 | 501898.8628 | 1.0566 | 1.3884
a | Common Area Electricity Expense | 142946.1463 | 0.30093 | 98607.6558 | 0.20759 | 0.50852 | 40071.331 | 0.084359 | 0.38529 | 150093.4536 | 0.31598 | 103538.0386 | 0.21797 | 0.53395 | 42074.8975 | 0.088577 | 0.40456 | 157598.1263 | 0.33178 | 108714.9405 | 0.22887 | 0.56065 | 44178.6424 | 0.093006 | 0.42478
b | HVAC Expense for common area |  | 0 | 556319.4771 | 1.1712 | 1.1712 | 415165.7328 | 0.87402 | 0.87402 | 0 | 0 | 584135.451 | 1.2297 | 1.2297 | 435924.0194 | 0.91772 | 0.91772 | 0 | 0 | 613342.2235 | 1.2912 | 1.2912 | 457720.2204 | 0.9636 | 0.9636
5 | Audits | 43333.3333 | 0.09 | 0 | 0 | 0.091226 | 0 | 0 | 0.091226 | 60833.3333 | 0.13 | 0 | 0 | 0.12807 | 0 | 0 | 0.12807 | 60833.3333 | 0.13 | 0 | 0 | 0.12807 | 0 | 0 | 0.12807
a | Energy Audit / Thermography and Harmonic Test | 8333.3333 | 0.017544 |  | 0 | 0.017544 |  | 0 | 0.017544 | 8333.3333 | 0.017544 |  | 0 | 0.017544 |  | 0 | 0.017544 | 8333.3333 | 0.017544 |  | 0 | 0.017544 |  | 0 | 0.017544
b | Fire, Health & Safety Audits | 8333.3333 | 0.017544 |  | 0 | 0.017544 |  | 0 | 0.017544 | 8333.3333 | 0.017544 |  | 0 | 0.017544 |  | 0 | 0.017544 | 8333.3333 | 0.017544 |  | 0 | 0.017544 |  | 0 | 0.017544
c | Indoor Air Quality and DG emmission testing | 8333.3333 | 0.017544 |  | 0 | 0.017544 |  | 0 | 0.017544 | 8333.3333 | 0.017544 |  | 0 | 0.017544 |  | 0 | 0.017544 | 8333.3333 | 0.017544 |  | 0 | 0.017544 |  | 0 | 0.017544
d | Legal and professional servcies | 8333.3333 | 0.017544 |  | 0 | 0.017544 |  | 0 | 0.017544 | 20833.3333 | 0.043859 |  | 0 | 0.043859 |  | 0 | 0.043859 | 20833.3333 | 0.043859 |  | 0 | 0.043859 |  | 0 | 0.043859
e | Statutory compliances (PF, ESIC, Ptax, Lab.Welfare, Licenses, Returns, Audit etc.) | 5000 | 0.010526 |  | 0 | 0.010526 |  | 0 | 0.010526 | 10000 | 0.021052 |  | 0 | 0.021052 |  | 0 | 0.021052 | 10000 | 0.021052 |  | 0 | 0.021052 |  | 0 | 0.021052
f | Water Testing Charges | 5000 | 0.010526 |  | 0 | 0.010526 |  | 0 | 0.010526 | 5000 | 0.010526 |  | 0 | 0.010526 |  | 0 | 0.010526 | 5000 | 0.010526 |  | 0 | 0.010526 |  | 0 | 0.010526
6 | Liosaning & Licenses Cost | 37891.6667 | 0.07977 | 0 | 0 | 0.07977 | 0 | 0 | 0.07977 | 37391.6667 | 0.078718 | 0 | 0 | 0.078718 | 0 | 0 | 0.078718 | 37391.6667 | 0.078718 | 0 | 0 | 0.078718 | 0 | 0 | 0.078718
a | Electrical and DG License renewal | 208.3333 | 0.00043859 |  | 0 | 0.00043859 |  | 0 | 0.00043859 | 208.3333 | 0.00043859 |  | 0 | 0.00043859 |  | 0 | 0.00043859 | 208.3333 | 0.00043859 |  | 0 | 0.00043859 |  | 0 | 0.00043859
b | Lift License Renewal | 2500 | 0.0052631 |  | 0 | 0.0052631 |  | 0 | 0.0052631 | 2000 | 0.0042104 |  | 0 | 0.0042104 |  | 0 | 0.0042104 | 2000 | 0.0042104 |  | 0 | 0.0042104 |  | 0 | 0.0042104
c | Fire NOC | 83.3333 | 0.00017544 |  | 0 | 0.00017544 |  | 0 | 0.00017544 | 83.3333 | 0.00017544 |  | 0 | 0.00017544 |  | 0 | 0.00017544 | 83.3333 | 0.00017544 |  | 0 | 0.00017544 |  | 0 | 0.00017544
d | Labour license and registration | 4166.6667 | 0.0087718 |  | 0 | 0.0087718 |  | 0 | 0.0087718 | 4166.6667 | 0.0087718 |  | 0 | 0.0087718 |  | 0 | 0.0087718 | 4166.6667 | 0.0087718 |  | 0 | 0.0087718 |  | 0 | 0.0087718
e | Liosaning & Licenses Cost | 25000 | 0.052631 |  | 0 | 0.052631 |  | 0 | 0.052631 | 25000 | 0.052631 |  | 0 | 0.052631 |  | 0 | 0.052631 | 25000 | 0.052631 |  | 0 | 0.052631 |  | 0 | 0.052631
f | Environmental and Pollution Control Inspections | 4166.6667 | 0.0087718 |  | 0 | 0.0087718 |  | 0 | 0.0087718 | 4166.6667 | 0.0087718 |  | 0 | 0.0087718 |  | 0 | 0.0087718 | 4166.6667 | 0.0087718 |  | 0 | 0.0087718 |  | 0 | 0.0087718
g | Water Cess | 1250 | 0.0026315 |  | 0 | 0.0026315 |  | 0 | 0.0026315 | 1250 | 0.0026315 |  | 0 | 0.0026315 |  | 0 | 0.0026315 | 1250 | 0.0026315 |  | 0 | 0.0026315 |  | 0 | 0.0026315
h | Shop & Etablishment ( 5years) | 100 | 0.00021052 |  | 0 | 0.00021052 |  | 0 | 0.00021052 | 100 | 0.00021052 |  | 0 | 0.00021052 |  | 0 | 0.00021052 | 100 | 0.00021052 |  | 0 | 0.00021052 |  | 0 | 0.00021052
i | Licesnse for storing Pertrolium | 416.6667 | 0.00087718 |  | 0 | 0.00087718 |  | 0 | 0.00087718 | 416.6667 | 0.00087718 |  | 0 | 0.00087718 |  | 0 | 0.00087718 | 416.6667 | 0.00087718 |  | 0 | 0.00087718 |  | 0 | 0.00087718
7 | Administrative Expenses | 70300 | 0.15 | 0 | 0 | 0.148 | 0 | 0 | 0.148 | 78300 | 0.16 | 0 | 0 | 0.16484 | 0 | 0 | 0.16484 | 78300 | 0.16 | 0 | 0 | 0.16484 | 0 | 0 | 0.16484
a | Rental Equipment (Photocopier, PC, Pumps etc) | 7000 | 0.014737 |  | 0 | 0.014737 |  | 0 | 0.014737 | 7000 | 0.014737 |  | 0 | 0.014737 |  | 0 | 0.014737 | 7000 | 0.014737 |  | 0 | 0.014737 |  | 0 | 0.014737
b | Travel / Conveyance | 5000 | 0.010526 |  | 0 | 0.010526 |  | 0 | 0.010526 | 5000 | 0.010526 |  | 0 | 0.010526 |  | 0 | 0.010526 | 5000 | 0.010526 |  | 0 | 0.010526 |  | 0 | 0.010526
c | Office Stationary and Printed Stationary | 10000 | 0.021052 |  | 0 | 0.021052 |  | 0 | 0.021052 | 18000 | 0.037894 |  | 0 | 0.037894 |  | 0 | 0.037894 | 18000 | 0.037894 |  | 0 | 0.037894 |  | 0 | 0.037894
d | Site Team Communication Charges-Mobile | 7000 | 0.014737 |  | 0 | 0.014737 |  | 0 | 0.014737 | 7000 | 0.014737 |  | 0 | 0.014737 |  | 0 | 0.014737 | 7000 | 0.014737 |  | 0 | 0.014737 |  | 0 | 0.014737
e | Magzine, Journals and Newspapers | 2800 | 0.0058946 |  | 0 | 0.0058946 |  | 0 | 0.0058946 | 2800 | 0.0058946 |  | 0 | 0.0058946 |  | 0 | 0.0058946 | 2800 | 0.0058946 |  | 0 | 0.0058946 |  | 0 | 0.0058946
f | Internet Broadband Connection | 5000 | 0.010526 |  | 0 | 0.010526 |  | 0 | 0.010526 | 5000 | 0.010526 |  | 0 | 0.010526 |  | 0 | 0.010526 | 5000 | 0.010526 |  | 0 | 0.010526 |  | 0 | 0.010526
g | Landline phone connection | 5000 | 0.010526 |  | 0 | 0.010526 |  | 0 | 0.010526 | 5000 | 0.010526 |  | 0 | 0.010526 |  | 0 | 0.010526 | 5000 | 0.010526 |  | 0 | 0.010526 |  | 0 | 0.010526
h | Staff Welfare for deployed manpower | 26000 | 0.054736 |  | 0 | 0.054736 |  | 0 | 0.054736 | 26000 | 0.054736 |  | 0 | 0.054736 |  | 0 | 0.054736 | 26000 | 0.054736 |  | 0 | 0.054736 |  | 0 | 0.054736
i | Courier Charges | 2500 | 0.0052631 |  | 0 | 0.0052631 |  | 0 | 0.0052631 | 2500 | 0.0052631 |  | 0 | 0.0052631 |  | 0 | 0.0052631 | 2500 | 0.0052631 |  | 0 | 0.0052631 |  | 0 | 0.0052631
8 | Insurance, Sinking Fund | 692061.6607 | 1.46 | 0 | 0 | 1.4569 | 0 | 0 | 1.4569 | 714037.4004 | 1.5 | 0 | 0 | 1.5032 | 0 | 0 | 1.5032 | 736892.1696 | 1.55 | 0 | 0 | 1.5513 | 0 | 0 | 1.5513
a | Insurance Fund ( Equipment & Structure) | 76001.5026 | 0.16 |  | 0 | 0.16 |  | 0 | 0.16 | 76001.5026 | 0.16 |  | 0 | 0.16 |  | 0 | 0.16 | 76001.5026 | 0.16 |  | 0 | 0.16 |  | 0 | 0.16
b | Sinking Fund | 549393.4915 | 1.1566 |  | 0 | 1.1566 |  | 0 | 1.1566 | 571369.2312 | 1.2029 |  | 0 | 1.2029 |  | 0 | 1.2029 | 594224.0004 | 1.251 |  | 0 | 1.251 |  | 0 | 1.251
c | Contigency Funds | 50000 | 0.10526 |  | 0 | 0.10526 |  | 0 | 0.10526 | 50000 | 0.10526 |  | 0 | 0.10526 |  | 0 | 0.10526 | 50000 | 0.10526 |  | 0 | 0.10526 |  | 0 | 0.10526
d | Insurance for Thrid Party liability | 16666.6667 | 0.035087 |  | 0 | 0.035087 |  | 0 | 0.035087 | 16666.6667 | 0.035087 |  | 0 | 0.035087 |  | 0 | 0.035087 | 16666.6667 | 0.035087 |  | 0 | 0.035087 |  | 0 | 0.035087
9 | Profit Margin 10% on Actual Expense | 353515.479 | 0.74423 | 128973.2445 | 0.68924 | 1.4335 | 64086.9726 | 0.22261 | 0.96684 | 396145.7536 | 0.83397 | 138094.5923 | 0.73799 | 1.572 | 86388.3718 | 0.30008 | 1.1341 | 452440.6754 | 0.95249 | 154022.6092 | 0.82311 | 1.7756 | 91464.546 | 0.31771 | 1.2702

## AMC Cost
ANNUAL MAINTENANCE CHARGE ESTIMATION- | [7 empty] | INDEX
S.No. as per Budget | Package No. | Package Name | DLP | 2nd Year | 3rd Year | 4th Year | 5th Year
1 | TIIPL/MEP-003(PART-1) | Fire Fighting |  | 559035 | 598167.45 | 640039.1715 | 684841.9135
2 | TIIPL/MEP-009 | FAS |  | 263130 | 281549.1 | 301257.537 | 322345.5646
|  | CCTV |  | 166000 | 177620 | 190053.4 | 203357.138
|  | IBMS&PAS |  | 208675 | 223282.25 | 238912.0075 | 255635.848
4 | TIIPL/MEP - 002 | Electrical Panels ( HT / LT) |  | 100000 | 105000 | 110250 | 115762.5
5 | TIIPL/MEP - 11 Part 1 | Fire Fighting Pumps | 0
6 | TIIPL/INT - 002 | Elevators | 0 | 0 | 3008333.3333 | 3218916.6667 | 3444240.8333
7 | TIIPL/MEP-005 | Diesel Generators | 0 | 0 | 200000 | 220000 | 242000
|  | IT Infrastructure- Computers |  | 240000 | 252000 | 264600 | 277830
|  | Annual Cost | 0 | 1536840 | 4845952.1333 | 5184028.7827 | 5546013.7975
|  | Monthly Cost | 0 | 128070 | 403829.3444 | 432002.3986 | 462167.8165
|  | Per sq ft Cost | 0 | 0.26962 | 0.85015 | 0.90946 | 0.97297
Office
| TIIPL/MEP -7(PART-2) | Package Units |  | 2200000 | 2300000 | 2400000 | 2600000
| Office Total | Monthly Cost | 0 | 183333.3333 | 191666.6667 | 200000 | 216666.6667
Mall
| TIIPL/MEP-007 | Chillers | 0 | 0 | 730000 | 730000 | 730000
| Mall Total | Monthly Cost | 0 | 0 | 60833.3333 | 60833.3333 | 60833.3333

## Comm Electrical load
ELECTRICAL EXPENSE CALCULATION |  |  |  | INDEX
COMM. UTILITIES
Common Area Electrcity Consumption
Total Unit Consumed per month | 19752.4686
Source | Rate per unit | Units Comsumed | Cost
DG Set | 18.29 | 1234.5293 | 22579.5407
UPPCL | 6.5 | 18517.9393 | 120366.6056
TOTAL UNIT CHARGES |  |  | 142946.1463
ELECTRICAL EXPENSE CALCULATION
MALL ELECTRICITY EXPENSES
Common Area Electrcity Consumption
Total Unit Consumed per month | 13625.7232
Source | Rate per unit | Units Comsumed | Cost
DG Set | 18.29 | 851.6077 | 15575.9049
UPPCL | 6.5 | 12774.1155 | 83031.7509
TOTAL UNIT CHARGES |  |  | 98607.6558
ELECTRICAL EXPENSE CALCULATION
OFFICE ELECTRICITY EXPENSES
Common Area Electrcity Consumption
Total Unit Consumed per month | 5537.1042
Source | Rate per unit | Units Comsumed | Cost
DG Set | 18.29 | 346.069 | 6329.6022
UPPCL | 6.5 | 5191.0352 | 33741.7287
TOTAL UNIT CHARGES |  |  | 40071.331

## Load Breakup
COMM. AREA ELECTRAL LOAD DETAIL - ELECTRICITY CONSUMPTION | [10 empty] | INDEX
Sl.No | DESCRIPTION OF AREA | EQUIPMENT DETAILS | CAPACITY IN KW | Diversity Factor-Load | Diversity Factor-Seasonal | Daily hrs of operation | Daily Units | Monthly units | Monthly Cost
Comm. Utilities
Lighting Load- Comm |  |  | 69.18 |  |  |  | 273.4486 | 8340.1811 |  | 66502.5189 | 798030.2266
1 | STAIRCASE | bulk head (11w) | 1.6 | 0.5 | 0.5 | 18 | 7.2 | 219.6
2 | LIFT SHAFT | bulk head (9w) | 1.78 | 0.2 | 0.5 | 1 | 0.178 | 5.429
3 | External Lighting |  | 10 | 0.7 | 0.5 | 10 | 35 | 1067.5
4 | Basement-1 | fluroscent lamp (2*28w) | 14.84 | 0.7 | 0.5 | 12 | 62.328 | 1901.004
|  | fluroscent lamp (1*28w) | 1.008 | 0.7 | 0.3 | 18 | 3.8102 | 116.2123
|  | fluroscent lamp (1*9w) | 0.108 | 0.7 | 0.5 | 18 | 0.6804 | 20.7522
5 | Basement-2 | fluroscent lamp (2*28w) | 8.288 | 0.7 | 0.5 | 12 | 34.8096 | 1061.6928
|  | fluroscent lamp (1*28w) | 4.9 | 0.7 | 0.3 | 18 | 18.522 | 564.921
6 | Basement-3 | fluroscent lamp (2*28w) | 12.152 | 0.7 | 0.5 | 12 | 51.0384 | 1556.6712
|  | fluroscent lamp (1*28w) | 1.372 | 0.7 | 0.3 | 18 | 5.1862 | 158.1779
7 | Basement-4 | fluroscent lamp (2*28w) | 12.04 | 0.7 | 0.5 | 12 | 50.568 | 1542.324
|  | fluroscent lamp (1*28w) | 1.092 | 0.7 | 0.3 | 18 | 4.1278 | 125.8967
Ventilation and Exhaust- Comm |  |  | 1057.8 |  |  |  | 112.3051 | 3425.3056 |  | 4200000
119 | DG- EXAUST AIR | AXIAL FAN | 15 | 0.5 | 0.7 | 0.1 | 0.525 | 16.0125
120 | DG- EXAUST AIR | AXIAL FAN | 15 | 0.5 | 0.7 | 0.1 | 0.525 | 16.0125
121 | DG- EXAUST AIR | AXIAL FAN | 15 | 0.5 | 0.7 | 0.1 | 0.525 | 16.0125
122 | DG- EXAUST AIR | AXIAL FAN | 15 | 0.5 | 0.7 | 0.1 | 0.525 | 16.0125
123 | DG-FRESH AIR | AXIAL FAN | 15 | 0.5 | 0.7 | 0.1 | 0.525 | 16.0125
124 | DG-FRESH AIR | AXIAL FAN | 15 | 0.5 | 0.7 | 0.1 | 0.525 | 16.0125
125 | DG-FRESH AIR | AXIAL FAN | 15 | 0.5 | 0.7 | 0.1 | 0.525 | 16.0125
126 | DG-FRESH AIR | AXIAL FAN | 15 | 0.5 | 0.7 | 0.1 | 0.525 | 16.0125
127 | TRASFORMER ROOM EXAUST AIR | AXIAL FAN | 2.2 | 0.5 | 0.7 | 11 | 8.47 | 258.335
128 | TRASFORMER ROOM EXAUST AIR | AXIAL FAN | 2.2 | 0.5 | 0.7 | 11 | 8.47 | 258.335
129 | HVAC PLANT ROOM FRESH AIR | AXIAL FAN | 5.5 | 0.25 | 0.7 | 12 | 11.55 | 352.275
130 | HVAC PLANT ROOM FRESH AIR | AXIAL FAN | 5.5 | 0.25 | 0.7 | 12 | 11.55 | 352.275
131 | HVAC PLANT ROOM EXAUST AIR | AXIAL FAN | 5.5 | 0.25 | 0.7 | 12 | 11.55 | 352.275
132 | HVAC PLANT ROOM EXAUST AIR | AXIAL FAN | 5.5 | 0.25 | 0.7 | 12 | 11.55 | 352.275
133 | PARKING EXHAUST | AXIAL FAN | 7.5 | 0.2 | 0.7 | 0.25 | 0.2625 | 8.0062
134 | PARKING EXHAUST | AXIAL FAN | 7.5 | 0.2 | 0.7 | 0.25 | 0.2625 | 8.0062
135 | PARKING EXHAUST | AXIAL FAN | 7.5 | 0.2 | 0.7 | 0.25 | 0.2625 | 8.0062
136 | PARKING FRESH AIR | AXIAL FAN | 7.5 | 0.2 | 0.7 | 0.25 | 0.2625 | 8.0062
137 | PARKING FRESH AIR | AXIAL FAN | 7.5 | 0.2 | 0.7 | 0.25 | 0.2625 | 8.0062
143 | BASEMENT-2 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
144 | BASEMENT-2 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
145 | BASEMENT-2 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
146 | BASEMENT-2 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
147 | BASEMENT-2 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
148 | BASEMENT-2 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
149 | BASEMENT-2 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
150 | BASEMENT-2 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
151 | BASEMENT-2 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
152 | BASEMENT-2 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
153 | BASEMENT-2 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
154 | BASEMENT-2 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
155 | BASEMENT-2 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
156 | BASEMENT-2 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
157 | BASEMENT-2 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
158 | BASEMENT-2 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
159 | BASEMENT-2 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
160 | BASEMENT-2 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
161 | BASEMENT-2 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
162 | BASEMENT-2 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
163 | BASEMENT-2 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
164 | BASEMENT-2 | AXIAL FAN | 15 | 0.2 | 0.7 | 0.1 | 0.21 | 6.405
165 | BASEMENT-2 | AXIAL FAN | 15 | 0.2 | 0.7 | 0.1 | 0.21 | 6.405
166 | BASEMENT-2 | AXIAL FAN | 15 | 0.2 | 0.7 | 0.1 | 0.21 | 6.405
167 | BASEMENT-2 | AXIAL FAN | 15 | 0.2 | 0.7 | 0.1 | 0.21 | 6.405
168 | BASEMENT-2 | AXIAL FAN | 15 | 0.2 | 0.7 | 0.1 | 0.21 | 6.405
169 | BASEMENT-3 | AXIAL FAN | 15 | 0.2 | 0.7 | 0.1 | 0.21 | 6.405
170 | BASEMENT-3 | AXIAL FAN | 15 | 0.2 | 0.7 | 0.1 | 0.21 | 6.405
171 | BASEMENT-3 | AXIAL FAN | 15 | 0.2 | 0.7 | 0.1 | 0.21 | 6.405
172 | BASEMENT-3 | AXIAL FAN | 15 | 0.2 | 0.7 | 0.1 | 0.21 | 6.405
173 | BASEMENT-3 | AXIAL FAN | 15 | 0.2 | 0.7 | 0.1 | 0.21 | 6.405
174 | BASEMENT-3 | AXIAL FAN | 15 | 0.2 | 0.7 | 0.1 | 0.21 | 6.405
175 | BASEMENT-3 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
176 | BASEMENT-3 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
177 | BASEMENT-3 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
178 | BASEMENT-3 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
179 | BASEMENT-3 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
180 | BASEMENT-3 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
181 | BASEMENT-3 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
182 | BASEMENT-3 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
183 | BASEMENT-3 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
184 | BASEMENT-3 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
185 | BASEMENT-3 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
186 | BASEMENT-3 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
187 | BASEMENT-3 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
188 | BASEMENT-3 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
189 | BASEMENT-3 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
190 | BASEMENT-3 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
191 | BASEMENT-3 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
192 | BASEMENT-3 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
193 | BASEMENT-3 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
194 | BASEMENT-3 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
195 | BASEMENT-3 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
196 | BASEMENT-4 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
197 | BASEMENT-4 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
198 | BASEMENT-4 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
199 | BASEMENT-4 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
200 | BASEMENT-4 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
201 | BASEMENT-4 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
202 | BASEMENT-4 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
203 | BASEMENT-4 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
204 | BASEMENT-4 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
205 | BASEMENT-4 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
206 | BASEMENT-4 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
207 | BASEMENT-4 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
208 | BASEMENT-4 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
209 | BASEMENT-4 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
210 | BASEMENT-4 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
211 | BASEMENT-4 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
212 | BASEMENT-4 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
213 | BASEMENT-4 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
214 | BASEMENT-4 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
215 | BASEMENT-4 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
216 | BASEMENT-4 | AXIAL FAN | 9.3 | 0.2 | 0.7 | 0.1 | 0.1302 | 3.9711
217 | BASEMENT-4 | AXIAL FAN | 15 | 0.2 | 0.7 | 0.1 | 0.21 | 6.405
218 | BASEMENT-4 | AXIAL FAN | 15 | 0.2 | 0.7 | 0.1 | 0.21 | 6.405
219 | BASEMENT-4 | AXIAL FAN | 15 | 0.2 | 0.7 | 0.1 | 0.21 | 6.405
220 | BASEMENT-4 | AXIAL FAN | 15 | 0.2 | 0.7 | 0.1 | 0.21 | 6.405
221 | BASEMENT-4 | AXIAL FAN | 15 | 0.2 | 0.7 | 0.1 | 0.21 | 6.405
222 | BASEMENT-4 | AXIAL FAN | 15 | 0.2 | 0.7 | 0.1 | 0.21 | 6.405
324 | STAIR PRESSURISATON-3 | AXIAL FAN | 4 | 0.2 | 1 | 0.2 | 0.16 | 4.88
325 | STAIR PRESSURISATON-4 | AXIAL FAN | 4 | 0.2 | 1 | 0.2 | 0.16 | 4.88
326 | STAIR PRESSURISATON-5 | AXIAL FAN | 4 | 0.2 | 1 | 0.2 | 0.16 | 4.88
327 | STAIR PRESSURISATON-1 | AXIAL FAN | 4 | 0.2 | 1 | 0.2 | 0.16 | 4.88
138 | ST-6 STAIRCASE PRESSURIZATION | AXIAL FAN | 7.5 | 0.2 | 1 | 0.2 | 0.3 | 9.15
142 | ST-3 STAIRCASE PRESSURIZATION | AXIAL FAN | 5.5 | 0.2 | 1 | 0.2 | 0.22 | 6.71
328 | STP EXAUST | AXIAL FAN | 4 | 0.8 | 0.8 | 12 | 30.72 | 936.96
63.1555
Sump Pumps- Comm |  |  | 50 |  |  |  | 3.125 | 95.3125 |  | 5.263
13 | Basement 4 | Catch Basin pump 1 | 5 | 0.5 | 0.5 | 0.25 | 0.3125 | 9.5312
14 | Basement 4 | Catch Basin pump 2 | 5 | 0.5 | 0.5 | 0.25 | 0.3125 | 9.5312
15 | Basement 4 | Catch Basin pump 3 | 5 | 0.5 | 0.5 | 0.25 | 0.3125 | 9.5312
16 | Basement 4 | Catch Basin pump 4 | 5 | 0.5 | 0.5 | 0.25 | 0.3125 | 9.5312
17 | Basement 4 | Catch Basin pump 5 | 5 | 0.5 | 0.5 | 0.25 | 0.3125 | 9.5312
18 | Basement 4 | Catch Basin pump 6 | 5 | 0.5 | 0.5 | 0.25 | 0.3125 | 9.5312
19 | Basement 4 | Catch Basin pump 7 | 5 | 0.5 | 0.5 | 0.25 | 0.3125 | 9.5312
20 | Basement 4 | Catch Basin pump 8 | 5 | 0.5 | 0.5 | 0.25 | 0.3125 | 9.5312
21 | Basement 4 | Catch Basin pump 9 | 5 | 0.5 | 0.5 | 0.25 | 0.3125 | 9.5312
22 | Basement 4 | Catch Basin pump 10 | 5 | 0.5 | 0.5 | 0.25 | 0.3125 | 9.5312
Fire Pumps |  |  | 239 |  |  |  | 1.2048 | 36.7452
1 | Basement 1 | Fire PUMP | 75 | 0.8 | 1 | 0.0059524 | 0.35714 | 10.8929
2 | Basement 1 | Fire PUMP | 75 | 0.8 | 1 | 0.0059524 | 0.35714 | 10.8929
3 | Basement 1 | Fire PUMP | 75 | 0.8 | 1 | 0.0059524 | 0.35714 | 10.8929
4 | Basement 1 | Fire PUMP | 4 | 0.8 | 1 | 0.011905 | 0.038095 | 1.1619
5 | Basement 1 | Fire PUMP | 4 | 0.8 | 1 | 0.011905 | 0.038095 | 1.1619
6 | Basement 1 | Fire PUMP | 3 | 0.8 | 1 | 0.011905 | 0.028571 | 0.87143
7 | Terrace | Fire PUMP | 3 | 0.8 | 1 | 0.011905 | 0.028571 | 0.87143
WTP |  |  | 73 |  |  |  | 118.86 | 3625.23
1 | Basement 1 | Hydro pnematic pump 1 | 11 | 0.25 | 0.7 | 6 | 11.55 | 352.275
2 | Basement 1 | Hydro pnematic pump 2 | 11 | 0.25 | 0.7 | 6 | 11.55 | 352.275
3 | Basement 1 | Hydro pnematic pump 3 | 11 | 0.25 | 0.7 | 6 | 11.55 | 352.275
4 | Basement 1 | Hydro pnematic pump 4 | 11 | 0.25 | 0.7 | 6 | 11.55 | 352.275
5 | Basement 1 | Domestic Pump 1 | 7.5 | 0.5 | 0.7 | 6 | 15.75 | 480.375
6 | Basement 1 | Domestic Pump 2 | 7.5 | 0.5 | 0.7 | 6 | 15.75 | 480.375
14 | Basement 4 | Pump | 4 | 0.7 | 0.7 | 6 | 11.76 | 358.68
15 | Basement 4 | Pump | 4 | 0.7 | 0.7 | 6 | 11.76 | 358.68
7 | Basement 1 | Raw Water pump 1 | 3 | 0.7 | 0.7 | 6 | 8.82 | 269.01
8 | Basement 1 | Raw Water pump 2 | 3 | 0.7 | 0.7 | 6 | 8.82 | 269.01
33333.3333
Raw Power Load |  |  | 16 |  |  |  | 2 | 61 |  | 0.070174
1 | Basement-4 | Mobile chargers,Vaccum cleaners etc. | 2 | 0.5 | 0.25 | 1 | 0.25 | 7.625
2 | Basement-3 | Mobile chargers,Vaccum cleaners etc. | 2 | 0.5 | 0.25 | 1 | 0.25 | 7.625
3 | Basement-2 | Mobile chargers,Vaccum cleaners etc. | 2 | 0.5 | 0.25 | 1 | 0.25 | 7.625
4 | Basement-1 | Mobile chargers,Vaccum cleaners etc. | 2 | 0.5 | 0.25 | 1 | 0.25 | 7.625
5 | Ground Floor | Mobile chargers,Vaccum cleaners etc. | 2 | 0.5 | 0.25 | 1 | 0.25 | 7.625
6 | Level-1 | Mobile chargers,Vaccum cleaners etc. | 2 | 0.5 | 0.25 | 1 | 0.25 | 7.625
7 | Level-2 | Mobile chargers,Vaccum cleaners etc. | 2 | 0.5 | 0.25 | 1 | 0.25 | 7.625
8 | Level-3 | Mobile chargers,Vaccum cleaners etc. | 2 | 0.5 | 0.25 | 1 | 0.25 | 7.625
STP |  |  | 71.11 |  |  |  | 136.6785 | 4168.6942
1 | Basement 4 | Reactor feed Pump | 1.5 | 0.5 | 0.7 | 6 | 3.15 | 96.075
2 | Basement 4 | Reactor feed Pump | 1.5 | 0.5 | 0.7 | 6 | 3.15 | 96.075
3 | Basement 4 | Roto Screw Pumps | 0.75 | 0.5 | 0.7 | 6 | 1.575 | 48.0375
4 | Basement 4 | Roto Screw Pumps | 0.75 | 0.5 | 0.7 | 6 | 1.575 | 48.0375
5 | Basement 4 | Filter Feed Pump | 5.5 | 0.5 | 0.7 | 6 | 11.55 | 352.275
6 | Basement 4 | Filter Feed Pump | 5.5 | 0.5 | 0.7 | 6 | 11.55 | 352.275
7 | Basement 4 (STP) | Sft water pump 1 | 7.5 | 0.25 | 0.7 | 6 | 7.875 | 240.1875
8 | Basement 4 (STP) | Sft water pump 2 | 7.5 | 0.25 | 0.7 | 6 | 7.875 | 240.1875
9 | Basement 4 (STP) | Sft water pump 3 | 7.5 | 0.25 | 0.7 | 6 | 7.875 | 240.1875
10 | Basement 4 (STP) | Sft water pump 4 | 7.5 | 0.25 | 0.7 | 6 | 7.875 | 240.1875
11 | Basement 4 | Softner feed Pump | 4 | 0.5 | 0.7 | 6 | 8.4 | 256.2
12 | Basement 4 | Softner feed Pump | 4 | 0.5 | 0.7 | 6 | 8.4 | 256.2
13 | Basement 4 | Air Blower Pumps | 5.5 | 0.4 | 0.7 | 12 | 18.48 | 563.64
14 | Basement 4 | Air Blower Pumps | 5.5 | 0.4 | 0.7 | 12 | 18.48 | 563.64
15 | Basement 4 | Air Blower Pumps | 5.5 | 0.4 | 0.7 | 12 | 18.48 | 563.64
16 | Basement 4 | Decander Pumps | 0.37 | 0.5 | 0.7 | 1 | 0.1295 | 3.9498
17 | Basement 4 | Decander Pumps | 0.37 | 0.5 | 0.7 | 1 | 0.1295 | 3.9498
18 | Basement 4 | Dosing Pump | 0.37 | 0.5 | 0.7 | 1 | 0.1295 | 3.9498
TOTAL ELECTRICAL LOAD FOR COMMON UTILITIES |  |  | 1576.09 |  |  |  | 647.6219 | 19752.4686 | 157501.2466
Mall
Lighting Load- Mall area common |  |  | 21.4258 |  |  |  | 130.713 | 3986.7472 |  | 31789.3257 | 381471.9089
1 | Ground Floor | combo light (45w) | 1.08 | 0.8 | 0.8 | 12 | 8.2944 | 252.9792
|  | strip light (9.6w) | 2.0275 | 0.8 | 0.8 | 12 | 15.5714 | 474.9263
|  | spot light (18w) | 0.936 | 0.8 | 0.8 | 12 | 7.1885 | 219.2486
2 | level-1 | combo light (45w) | 0.9 | 0.8 | 0.5 | 12 | 4.32 | 131.76
| - | strip light (9.6w) | 2.4067 | 0.8 | 0.8 | 12 | 18.4836 | 563.7501
| - | spot light (18w) | 1.404 | 0.8 | 0.5 | 12 | 6.7392 | 205.5456
3 | level-2 | combo light (45w) | 1.395 | 0.8 | 0.5 | 12 | 6.696 | 204.228
|  | strip light (9.6w) | 2.207 | 0.8 | 0.8 | 12 | 16.9501 | 516.977
|  | spot light (18w) | 1.098 | 0.8 | 0.5 | 12 | 5.2704 | 160.7472
|  | RD(LED accent light)(26w) | 0.52 | 0.8 | 0.5 | 12 | 2.496 | 76.128
4 | level-3 | strip light (9.6w) | 1.0195 | 0.8 | 0.8 | 12 | 7.8299 | 238.8124
|  | spot light (18w) | 3.456 | 0.8 | 0.5 | 12 | 16.5888 | 505.9584
|  | linear lights (24w) | 2.976 | 0.8 | 0.5 | 12 | 14.2848 | 435.6864
Lift- Mall |  |  | 173.6 |  |  |  | 316.032 | 9638.976
1 | Basement 1 | Travalator 1 | 9 | 0.2 | 0.5 | 12 | 10.8 | 329.4
2 | Basement 1 | Travalator 2 | 9 | 0.2 | 0.5 | 12 | 10.8 | 329.4
3 | Level Ground | Travalator 3 | 9 | 0.2 | 0.5 | 12 | 10.8 | 329.4
4 | Level 1 | Travalator 4 | 9 | 0.2 | 0.5 | 12 | 10.8 | 329.4
5 | Level 1 | Travalator 5 | 9 | 0.2 | 0.5 | 12 | 10.8 | 329.4
6 | Level 1 | Escalator 1 | 7.5 | 0.35 | 0.5 | 12 | 15.75 | 480.375
7 | Level 1 | Escalator 2 | 7.5 | 0.35 | 0.5 | 12 | 15.75 | 480.375
8 | Level 2 | Escalator 3 | 7.5 | 0.35 | 0.5 | 12 | 15.75 | 480.375
9 | Level 2 | Escalator 4 | 7.5 | 0.35 | 0.5 | 12 | 15.75 | 480.375
10 | Level 3 | Escalator 5 | 7.5 | 0.35 | 0.5 | 12 | 15.75 | 480.375
11 | Level 3 | Escalator 6 | 7.5 | 0.35 | 0.5 | 12 | 15.75 | 480.375
12 | Level 3 | Mall Guest Lift 1 | 19.5 | 0.35 | 0.5 | 12 | 40.95 | 1248.975
13 | Level 3 | Mall Guest Lift 2 | 19.5 | 0.35 | 0.5 | 12 | 40.95 | 1248.975
14 | Level 3 | Mall Sevice Lift 1 | 22.3 | 0.2 | 0.8 | 12 | 42.816 | 1305.888
15 | Level 3 | Mall Sevice Lift 2 | 22.3 | 0.2 | 0.8 | 12 | 42.816 | 1305.888
TOTAL ELECTRICAL LOAD FOR COMMON UTILITIES |  |  | 195.0258 |  |  |  | 446.745 | 13625.7232 | 108648.1106
Office
Lighting Load- Office Area common |  |  | 2.214 |  |  |  | 21.2544 | 648.2592 |  | 5169.0568 | 62028.6816
1 | Level-4 | spot light (18w) | 0.414 | 0.8 | 1 | 12 | 3.9744 | 121.2192
2 | Level-5 | spot light (18w) | 0.504 | 0.8 | 1 | 12 | 4.8384 | 147.5712
3 | Level-6 | spot light (18w) | 0.432 | 0.8 | 1 | 12 | 4.1472 | 126.4896
4 | Level-7 | spot light (18w) | 0.432 | 0.8 | 1 | 12 | 4.1472 | 126.4896
5 | Level-8 | spot light (18w) | 0.432 | 0.8 | 1 | 12 | 4.1472 | 126.4896
Lift-Office |  |  | 78 |  |  |  | 160.29 | 4888.845
5 | Level 09 | Office Elevator 1 | 19.5 | 0.35 | 0.5 | 12 | 40.95 | 1248.975
6 | Level 09 | Office Elevator 2 | 19.5 | 0.35 | 0.5 | 12 | 40.95 | 1248.975
7 | Level 09 | Office Elevator 3 | 19.5 | 0.35 | 0.5 | 12 | 40.95 | 1248.975
8 | Level 09 | Office Service Elevator | 19.5 | 0.2 | 0.8 | 12 | 37.44 | 1141.92
TOTAL ELECTRICAL LOAD FOR COMMON UTILITIES |  |  | 80.214 |  |  |  | 181.5444 | 5537.1042 | 44151.4846
Office- HVAC Load
44 | Level 4 | 5.5 TR Package Unit | 5 | 0.8 | 0.7 | 12 | 33.6 | 873.6
59 | Level 5 | 5.5 TR Package Unit | 5 | 0.8 | 0.7 | 12 | 33.6 | 873.6
85 | Level 6 | 8.75 TR Package Unit | 7 | 0.8 | 0.7 | 12 | 47.04 | 1223.04
93 | Level 7 | 5.5 TR Package Unit | 5 | 0.8 | 0.7 | 12 | 33.6 | 873.6
118 | Level 8 | 8.75 TR Package Unit | 7 | 0.8 | 0.7 | 12 | 47.04 | 1223.04
15 | Terrace | Condenser Water pump -1 ( Office ) | 75 | 0.8 | 0.7 | 12 | 504 | 13104
16 | Terrace | Condenser Water pump -2 (Office ) | 75 | 0.8 | 0.7 | 12 | 504 | 13104
17 | Terrace | Condenser Water pump -3 ( Office ) | 75 | 0.8 | 0.7 | 12 | 504 | 13104
18 | Terrace | Cooling Tower 1 (Office ) Fan1 | 5.5 | 0.8 | 0.7 | 12 | 36.96 | 960.96
19 | Terrace | Cooling Tower 1 (Office ) Fan2 | 5.5 | 0.8 | 0.7 | 12 | 36.96 | 960.96
20 | Terrace | Cooling Tower 1 (Office ) Fan3 | 5.5 | 0.8 | 0.7 | 12 | 36.96 | 960.96
21 | Terrace | Cooling Tower 1 (Office ) Fan4 | 5.5 | 0.8 | 0.7 | 12 | 36.96 | 960.96
22 | Terrace | Cooling Tower 2 (Office ) Fan1 | 5.5 | 0.8 | 0.7 | 12 | 36.96 | 960.96
23 | Terrace | Cooling Tower 2 (Office ) Fan2 | 5.5 | 0.8 | 0.7 | 12 | 36.96 | 960.96
24 | Terrace | Cooling Tower 2 (Office ) Fan3 | 5.5 | 0.8 | 0.7 | 12 | 36.96 | 960.96
25 | Terrace | Cooling Tower 2 (Office ) Fan4 | 5.5 | 0.8 | 0.7 | 12 | 36.96 | 960.96
|  | Total Load | 298 |  | Total Units |  |  | 52066.56
[5 empty] | Unit Rate |  |  | 7.9737
[5 empty] | Total Cost per Montrh |  |  | 415165.7328
HVAC Load- Mall Area
1 | Basement - 1 | 610TR Water Cooled Centrifugal Chiller | 390
2 | Basement - 1 | 610TR Water Cooled Centrifugal Chiller | 390
3 | Basement - 1 | 350TR Water Cooled Screw Chiller | 243
4 | Basement - 1 | Primary pump-1 | 18.5
5 | Basement - 1 | Primary pump-2 | 18.5
6 | Basement - 1 | Primary pump-3 | 15
7 | Basement - 1 | Seconary pump - 1 | 22
8 | Basement - 1 | Seconary pump - 2 | 22
9 | Basement - 1 | Seconary pump - 3 | 22
10 | Basement - 1 | Seconary pump - 4 | 22
11 | Basement - 1 | Seconary pump - 5 | 22
12 | Basement - 1 | Condenser Water pump - 1 | 45
13 | Basement - 1 | Condenser Water pump - 2 | 45
14 | Basement - 1 | Condenser Water pump - 3 | 22
26 | Terrace | Cooling Tower 1 ( Mall ) Fan1 | 5.5
27 | Terrace | Cooling Tower 1 ( Mall ) Fan2 | 5.5
28 | Terrace | Cooling Tower 1 ( Mall ) Fan3 | 5.5
29 | Terrace | Cooling Tower 1 ( Mall ) Fan4 | 5.5
30 | Terrace | Cooling Tower 2 ( Mall ) Fan1 | 5.5
31 | Terrace | Cooling Tower 2 ( Mall ) Fan2 | 5.5
32 | Terrace | Cooling Tower 2 ( Mall ) Fan3 | 5.5
33 | Terrace | Cooling Tower 2 ( Mall ) Fan4 | 5.5
34 | Terrace | Cooling Tower 3 ( Mall ) Fan 1 | 5.5
35 | Terrace | Cooling Tower 3 ( Mall ) Fan 2 | 5.5
|  | Total Load | 1352

## HVAC-Mall
HVAC CHARGES CALCULATION
Description |  | Mall |  |  | Aux. Pumps | Mani |  | Total | Standby | INDEX
Airconditioned Area | Comm. Area | 34613.5795 |  |  | PRIMARY | 18.5 | 15 | 33.5 | 18.5
| Leased Area | 84205.5162 |  |  | Secondary- Comm. | 22 | 22 | 44 | 22
| Total Area | 118819.0957 | 187123.3693 |  | Condenser | 45 | 22 | 67 | 44
Chiller Tonage | TOTAL (TR) | 960 | 587.9006 | 50% | Cooling Towers | 22 | 11 | 33 | 22
Electrical Load-Chiller (IKW / TR) | 0.63 | 604.8 | 202.1075 |  |  | 107.5 |  | 177.5
Chiller Loading / unloading factor in 12 hrs operation | 61.24% | 370.3774
Auxillary Pump Load | 0.73032 | 129.6321 | 35%
Total Connected Load |  | 500.0095
Electricity Cost-State Electricity Board |  | 6.5
Electricity Cost-DG Power |  | 18.29
Power Cut in Hrs (in 12 hrs) |  | 1.5
Average Cost for Power unit |  | 7.9737
Total Cost per hr |  | 3986.9504
Total Cost per day (12 hrs operation) |  | 47843.4047
Total Cost per month |  | 1459223.8446
Cost per ton per month |  | 1520.0248
AC cost per sq. ft per month |  | 12.2811
Seasonal Diversity Factor |  | 0.7
Final AC cost per sq. ft per month | INR | 8.5967
AC Charges for Common Area per month |  | 1021456.6912
Cost for HVAC of Common Area in sq ft- Chiller | 51920.3693 | 446345.8361
Cost of AHU- Comm Area |  | 109973.6411
556319.4771
Cost for HVAC for Tenants inside Mall
Leasable Area inside Mall | Sq ft | 187123.3693
Cost for Air conditioning excluding Comm. Area cost | INR | 575110.8552
3.0734

## Mall AHU Load
ELECTRICAL LOAD OF AHU / FCU
Sr. No | LOCATION | TYPE | MAKE | Sr. No | CAPACITY IN KW | Diversity Factor-Load | Diversity Factor-Seasonal | Daily hrs of operation | Daily Units | Monthly units | INDEX
1 | BOH CSU | CSU | ZECO | 1341110 | 1.5 | 0.7 | 0.5 | 12 | 6.3 | 163.8
2 | BOH CSU | CSU | ZECO | 1341111 | 1.5 | 0.7 | 0.5 | 12 | 6.3 | 163.8
3 | GROUND FLOOR | LG | LTI | 13/055/041 | 5.5 | 0.7 | 0.5 | 12 | 23.1 | 600.6
4 | GROUND FLOOR | LG | LTI | 13/055/042 | 5.5 | 0.7 | 0.5 | 12 | 23.1 | 600.6
5 | GROUND FLOOR | LG | LTI | 13/055/043 | 5.5 | 0.7 | 0.5 | 12 | 23.1 | 600.6
6 | GROUND FLOOR | LG | LTI | 13/055/044 | 5.5 | 0.7 | 0.5 | 12 | 23.1 | 600.6
7 | LEVEL-1 | CORRIDOR | ZECO | 1341106-2 | 3.7 | 0.7 | 0.5 | 12 | 15.54 | 404.04
8 | LEVEL-1 | LI - LVL | ZECO | 1341105-1 | 7.5 | 0.7 | 0.5 | 12 | 31.5 | 819
9 | LEVEL-1 | LI - LVL | ZECO | 1341105-2 | 7.5 | 0.7 | 0.5 | 12 | 31.5 | 819
10 | LEVEL-1 | LI - LVL | ZECO | 1341105-3 | 7.5 | 0.7 | 0.5 | 12 | 31.5 | 819
11 | LEVEL-1 | LI - LVL | ZECO | 1341124 | 7.5 | 0.7 | 0.5 | 12 | 31.5 | 819
12 | LEVEL-2 | CORRIDOR | ZECO | 134110601 | 3.7 | 0.7 | 0.5 | 12 | 15.54 | 404.04
13 | LEVEL-2 | L2 - LVL | LTI | 13/055/013 | 5.5 | 0.7 | 0.5 | 12 | 23.1 | 600.6
14 | LEVEL-2 | L2 - LVL | LTI | 13/055/035 | 5.5 | 0.7 | 0.5 | 12 | 23.1 | 600.6
15 | LEVEL-2 | L2 - LVL | LTI | 13/055/050 | 5.5 | 0.7 | 0.5 | 12 | 23.1 | 600.6
16 | LEVEL-2 | L2 - LVL | LTI | 13/055/036 | 5.5 | 0.7 | 0.5 | 12 | 23.1 | 600.6
17 | LEVEL-2 | LOFT | ZECO | 1341107-28 | 3.7 | 0.7 | 0.5 | 12 | 15.54 | 404.04
18 | LEVEL-3 | CORRIDOR | ZECO | 1341122 | 3.7 | 0.7 | 0.5 | 12 | 15.54 | 404.04
19 | LEVEL-3 | CORRIDOR | ZECO | 1341123 | 5.5 | 0.7 | 0.5 | 12 | 23.1 | 600.6
20 | LEVEL-3 | L3 - LVL | ZECO | 1341108 | 5.5 | 0.7 | 0.5 | 12 | 23.1 | 600.6
21 | LEVEL-3 | L3 - LVL | ZECO | 1341119-5 | 5.5 | 0.7 | 0.5 | 12 | 23.1 | 600.6
22 | LEVEL-3 | L3 - LVL | ZECO | 1341116-3 | 7.5 | 0.7 | 0.5 | 12 | 31.5 | 819
23 | LEVEL-3 | L3 - LVL | ZECO | 13411051 | 7.5 | 0.7 | 0.5 | 12 | 31.5 | 819
24 | PANEL ROOM CSU | CSU | ZECO | 1341118-2 | 3 | 0.7 | 0.5 | 12 | 12.6 | 327.6
|  |  |  | Total Units consumed |  |  | Total Units |  |  | 13791.96
|  |  |  | Per unit Cost |  |  | Unit Rate |  |  | 7.9737
|  |  |  | Cost per month |  |  | Total Cost per Montrh |  |  | 109973.6411

## Manpower
|  | MANPOWER DEPLOYMENT PLAN AND COSTING |  |  |  | 100% occupancy
Designation | Service Deployment Area | Designation |  |  | Monthly Unit Cost | SHIFT |  |  |  |  | Total | Monthly Cost | INDEX
[6 empty] | A | B | C | Gen | Rel
Management Staff |  | Property Management Staff
GM Operations |  | GM Operations |  | 720000 | 60000 |  |  |  | 1 |  | 1 | 60000
Finance Manager |  | Finance Manager |  | 720000 | 60000 |  |  |  | 1 |  | 1 | 60000
Manager- Marketing |  | Manager- Marketing |  | 720000 | 60000 |  |  |  | 1 |  | 1 | 60000
Sub Total C&W staff Cost (A) |  | Sub Total C&W staff Cost (A) |  |  |  | 0 | 0 | 0 | 3 | 0 | 3 | 180000 | 0.37894
C&W Management Staff |  | Property Management Staff
Property Manager |  | Property Manager |  | 900000 | 75000 |  |  |  | 1 |  | 1 | 75000
Manager- | Accounts and Finance | Manager- Accounts and Finance |  | 600000 | 50000 | [5 empty] | 0 | 0
Executive- | Purchase & Store | Executive-Purchase & Store | 360000 | 250000 | 20833.3333 |  |  |  | 1 |  | 1 | 20833.3333
Manager- | Engineering Services | Manager-Engineering Services | 900000 | 600000 | 50000 |  |  |  | 1 |  | 1 | 50000
Shift Engineers | Technical Services | Shift EngineersTechnical Services |  | 250000 | 20833.3333 | 1 | 1 | 1 |  |  | 3 | 62500
Manager- | Custodial Services | Manager-Custodial Services | 900000 | 600000 | 50000 |  |  |  | 1 |  | 1 | 50000
Facility Executive- | General Cleaning & Housekeeping | Facility Executive-General Cleaning & Housekeeping |  | 300000 | 25000 | 1 | 1 |  |  |  | 2 | 50000
Facility Executive- | Help Desk | Facility Executive-Help Desk |  | 250000 | 20833.3333 | 1 | 1 | 1 |  | 1 | 4 | 83333.3333
Manager- | Security and Fire Safety | Manager-Security and Fire Safety |  | 500000 | 41666.6667 |  |  |  | 1 |  | 1 | 41666.6667
Security & Fire Officer |  | Security & Fire Officer |  | 250000 | 20833.3333 | 1 | 1 | 1 |  |  | 3 | 62500
Sub Total C&W staff Cost (A) |  | Sub Total C&W staff Cost (A) |  |  |  | 4 | 4 | 3 | 5 | 1 | 17 | 495833.3333 | 1.0438 | 0.6263
Engineering Services (8hrs X 6 days a week) |  | Engineering Services (8hrs X 6 days a week)
Technical Supervisor |  | Technical Supervisor |  | 224952 | 18746 | 1 | 1 | 1 |  | 1 | 4 | 74984
Multi skill Technicians |  | Multi skill Technicians |  | 196800 | 16400 | 2 | 2 | 1 |  | 1 | 6 | 98400
BMS Operator |  | BMS Operator |  | 196800 | 16400 | 1 | 1 | 1 |  |  | 3 | 49200
HVAC Technician |  | HVAC Technician |  | 196800 | 16400 | 2 | 2 | 1 |  | 1 | 6 | 98400
Plumber |  | Plumber |  | 196800 | 16400 | 1 | 1 | 1 |  | 1 | 4 | 65600
Carpenter |  | Carpenter |  | 196800 | 16400 |  |  |  | 1 |  | 1 | 16400
Painter |  | Painter |  | 196836 | 16403 |  |  |  | 1 |  | 1 | 16403
Masson |  | Masson |  | 196860 | 16405 | [5 empty] | 0 | 0
Painter |  | Painter |  | 196836 | 16403 |  |  |  | 1 |  | 1 | 16403
Technical Helper |  | Technical Helper |  | 147504 | 12292 | 1 | 1 | 1 |  | 1 | 4 | 49168
Valet Driver |  | Valet Driver |  | 175704 | 14642 |  |  |  | 6 |  | 6 | 87852
Sub Total (B) - Engineering Services |  | Sub Total (B) - Engineering Services | 0 |  |  | 8 | 8 | 6 | 9 | 5 | 36 | 572810 | 1.2059 | 0.96471
Custodial Services (HK and General Cleaning Servcies) (8hrs X 6 days a week)- Comm |  | Custodial Services (HK and General Cleaning Servcies) (8hrs X 6 days a week)- Comm
Runner |  | Runner |  | 161412 | 13451 |  |  |  | 1 |  | 1 | 13451
Pantry Boy | Back Office | Pantry Boy Back Office |  | 161412 | 13451 |  |  |  | 1 |  | 1 | 13451
Housekeeping Supervisor |  | Housekeeping Supervisor |  | 239028 | 19919 | 0.5 | 0.5 | 0.25 |  | 0.3 | 1.55 | 30874.45
Janitors | Outer Periphery | Janitors Outer Periphery |  | 128448 | 10704 | 2 | 2 | 2 |  |  | 6 | 64224
Janitors | B1- B4 & Utilities | Janitors B1- B4 & Utilities |  | 128448 | 10704 |  |  |  |  | 1 | 1 | 10704
Sub Total (C) - Custodial Services |  | Sub Total (C) - Housekeeping Services |  |  |  | 2.5 | 2.5 | 2.25 | 2 | 1.3 | 10.55 | 132704.45 | 0.27937 | 0.13969
Custodial Services (HK and General Cleaning Servcies) (8hrs X 6 days a week)- Mall |  | Custodial Services (HK and General Cleaning Servcies) (8hrs X 6 days a week)- Mall
Housekeeping Supervisor |  | Housekeeping Supervisor |  | 239028 | 19919 | 1 | 1 | 0.5 |  | 0.4 | 2.9 | 57765.1
Janitors | L1- L3 | Janitors L1- L3 |  | 128448 | 10704 | 6 | 6 | 4 |  |  | 16 | 171264
Janitors | Comm Toilets | Janitors Comm Toilets |  | 128448 | 10704 | 2 | 2 |  |  | 3 | 7 | 74928
Sub Total (C) - Custodial Services |  | Sub Total (C) - Housekeeping Services |  |  |  | 9 | 9 | 4.5 | 0 | 3.4 | 25.9 | 303957.1 | 0.6399 | 0.31995
Custodial Services (HK and General Cleaning Servcies) (8hrs X 6 days a week)- Office |  | Custodial Services (HK and General Cleaning Servcies) (8hrs X 6 days a week)- Office
Housekeeping Supervisor |  | Housekeeping Supervisor |  | 239028 | 19919 | 0.5 | 0.5 | 0.25 |  | 0.3 | 1.55 | 30874.45
Janitors | L4-L8 | Janitors L4-L8 |  | 128448 | 10704 | 2 | 2 | 2 |  |  | 6 | 64224
Sub Total (C) - Custodial Services |  | Sub Total (C) - Housekeeping Services |  |  |  | 2.5 | 2.5 | 2.25 | 0 | 0.3 | 7.55 | 95098.45 | 0.2002
Outsourced Services ( Horticulture Manpower) (8hrs X 6 days a week) |  | Outsourced Services ( Horticulture Manpower) (8hrs X 6 days a week)
Head Gardner |  | Head Gardner |  | 224952 | 18746 |  |  |  | 1 |  | 1 | 18746
Gardner | Common Area | GardnerCommon Area |  | 161412 | 13451 |  |  |  | 2 |  | 2 | 26902
Sub Total (D) - Horticulture Services |  | Sub Total (D) - Horticulture Services | [8 empty] | 3 | 45648 | 0.096099
Outsourced Services ( Horticulture Consumables) (8hrs X 6 days a week) |  | Outsourced Services ( Horticulture Consumables) (8hrs X 6 days a week)
Tools and Equipments |  | Tools and Equipments | [9 empty] | 3000
|  | Potted Plants Costing | [9 empty] | 18000
Manure, Chemicals and Saplings |  | Manure, Chemicals and Saplings | [9 empty] | 8000
Sub Total (E) - Horticulture Services |  | Sub Total (E) - Horticulture Services | [8 empty] | 1 | 29000 | 0.061051
( Security Servcies) (8hrs X 6 days a week)- Comm |  | ( Security Servcies) (8hrs X 6 days a week)- Comm
Security Supervisor | Main Entry | Security Supervisor Main Entry |  | 168216 | 14018 | 1 | 1 | 1 |  | 1 | 4 | 56072
Head Guard | Control Room | Head Guard Control Room |  | 168216 | 14018 | 1 | 1 | 1 |  |  | 3 | 42054
Security Guard | Entry & Exit Point | Security Guard Entry & Exit Point |  | 138348 | 11529 | 1 | 1 | 1 |  |  | 3 | 34587
Security Guard | Campus Perifery & Drive Ways | Security Guard Campus Perifery & Drive Ways |  | 138348 | 11529 | 2 | 2 | 1 | 2 |  | 7 | 80703
Security Guard | Basement 1 ( Lift Lobbies) | Security Guard Basement 1 ( Lift Lobbies) |  | 138348 | 11529 | 1 | 1 | 1 | 1 |  | 4 | 46116
Security Guard | Basement 2 ( Lift Lobbies) | Security Guard Basement 2 ( Lift Lobbies) |  | 138348 | 11529 | 1 | 1 | 0 | 1 |  | 3 | 34587
Security Guard | Basement 3 ( Lift Lobbies) | Security Guard Basement 3 ( Lift Lobbies) |  | 138348 | 11529 | 1 | 1 | 0 | 3 |  | 5 | 57645
Security Guard | Basement 4 ( Lift Lobbies) | Security Guard Basement 4 ( Lift Lobbies) |  | 138348 | 11529 | 1 | 1 | 0 | 3 | 5 | 10 | 115290
Sub Total (F) - Security Services |  | Sub Total (F) - Security Services |  |  |  | 9 | 9 | 5 | 10 | 6 | 39 | 467054 | 0.98325
( Security Servcies) (8hrs X 6 days a week)- Mall |  | ( Security Servcies) (8hrs X 6 days a week)- Mall
Security Guard | Grd Floor- Mall Entry Outside | Security Guard Grd Floor- Mall Entry Outside |  | 138348 | 11529 |  |  | 2 | 2 |  | 4 | 46116
Security Guard | Mall Atrium Gate | Security Guard Mall Atrium Gate |  | 138348 | 11529 | 2 | 2 | 1 | 1 |  | 6 | 69174
Security Guard | LG-L3- Mall | Security Guard LG-L3- Mall |  | 138348 | 11529 | 3 | 3 | 1 |  | 3 | 10 | 115290
Sub Total (G) - Security Services |  | Sub Total (F) - Security Services |  |  |  | 5 |  | 4 | 3 |  | 20 | 230580 | 0.48542
( Security Servcies) (8hrs X 6 days a week)- Office |  | ( Security Servcies) (8hrs X 6 days a week)- Office
Security Guard | Grd Floor- Office Entry | Security Guard Grd Floor- Office Entry |  | 138348 | 11529 | 2 | 2 | 1 |  |  | 5 | 57645
Sub Total (H) - Security Services |  | Sub Total (F) - Security Services |  |  |  | 2 |  | 1 | 0 |  | 5 | 57645 | 0.12136
( Façade Cleaning Servcies) (8hrs X 6 days a week) |  | ( Façade Cleaning Servcies) (8hrs X 6 days a week)
Façade Cleaning Supervisor |  | Façade Cleaning Supervisor |  | 168216 | 14018 |  |  |  |  | 1 | 1 | 14018
Cradle Operator |  | Cradle Operator |  | 168216 | 14018 |  |  |  |  | 1 | 1 | 14018
Façade Cleaner |  | Façade Cleaner |  | 168216 | 14018 |  |  |  |  | 2 | 2 | 28036
Spiderman |  | Spiderman |  | 168216 | 14018 |  |  |  |  | 1 | 1 | 14018
Helpers |  | Helpers |  | 118344 | 9862 |  |  |  |  | 1 | 1 | 9862
Spideman Tool Kit |  | Spideman Tool Kit |  |  | 2500 | [5 empty] | 2 | 5000
Sub Total (I) - Façade Cleaning Services |  | Sub Total (F) - Security Services |  |  |  | 0 | 0 | 0 | 0 | 6 | 8 | 84952 | 0.17884

## Salary Breakup
Salary Breakup- Hyderabad
SALARY DETAILS |  |  | ENGINEERING SERVICES | [13 empty] | HK Services |  |  |  | Horticulture |  | Façade Cleaning |  |  |  |  | Security |  |  | INDEX
Designation |  |  | Technical Supervisor | Multi skill Technicians | Electrician | DG Operator | BMS Operator | HVAC Technician | HVAC Operators | Plumber | Carpenter | Painter | Masson | Painter | Technical Helper | Valet Driver | Housekeeping Supervisor | Pantry Boy | Runner | Janitors | Head Gardner | Gardner | Façade Cleaning Supervisor | Cradle Operator | Façade Cleaner | Spiderman | Helpers | Security Supervisor | Head Guard | Security Guard
Employee Category |  |  | Skilled | Skilled | Skilled | Skilled | Skilled | Skilled | Skilled | Skilled | Skilled | Skilled | Skilled | Skilled | SemiSkilled | SemiSkilled | Skilled | SemiSkilled | SemiSkilled | unskilled | Skilled | SemiSkilled | Skilled | Skilled | Skilled | Skilled | unskilled | Skilled | Skilled | Semiskilled
GROSS SALARY
Basic |  |  | 8079 | 8079 | 8079 | 8079 | 8079 | 8079 | 8079 | 8079 | 8079 | 8079 | 8079 | 8079 | 6579 | 6579 | 8079 | 6579 | 6579 | 5579 | 8079 | 6579 | 8079 | 8079 | 8079 | 8079 | 5579 | 8079 | 8079 | 6579
DA |  |  | 1739 | 1739 | 1739 | 1739 | 1739 | 1739 | 1739 | 1739 | 1739 | 1739 | 1739 | 1739 | 1419 | 1419 | 1739 | 1419 | 1419 | 1199 | 1739 | 1419 | 1739 | 1739 | 1739 | 1739 | 1199 | 1739 | 1739 | 1419
BASIC & DA |  |  | 9818 | 9818 | 9818 | 9818 | 9818 | 9818 | 9818 | 9818 | 9818 | 9818 | 9818 | 9818 | 7998 | 7998 | 9818 | 7998 | 7998 | 6778 | 9818 | 7998 | 9818 | 9818 | 9818 | 9818 | 6778 | 9818 | 9818 | 7998
Conv.
HRA
Special Allowance |  |  | 4103.0687 | 2067.4453 | 2067.4453 | 2067.4453 | 2067.4453 | 2067.4453 | 2067.4453 | 2067.4453 | 2067.4453 | 2067.4453 | 2067.4453 | 2067.4453 | 650.8041 | 2686.4275 | 5120.8804 | 1668.6158 | 1668.6158 | 730.855 | 4103.0687 | 1668.6158
SUB TOTAL |  |  | 13921.0687 | 11885.4453 | 11885.4453 | 11885.4453 | 11885.4453 | 11885.4453 | 11885.4453 | 11885.4453 | 11885.4453 | 11885.4453 | 11885.4453 | 11885.4453 | 8648.8041 | 10684.4275 | 14938.8804 | 9666.6158 | 9666.6158 | 7508.855 | 13921.0687 | 9666.6158 | 9818 | 9818 | 9818 | 9818 | 6778 | 9818 | 9818 | 7998
COMPLIANCES
Employee | ESI | 1.75% | 243.6187 | 207.9953 | 207.9953 | 207.9953 | 207.9953 | 207.9953 | 207.9953 | 207.9953 | 207.9953 | 207.9953 | 207.9953 | 207.9953 | 151.3541 | 186.9775 | 261.4304 | 169.1658 | 169.1658 | 131.405 | 243.6187 | 169.1658 | 171.815 | 171.815 | 171.815 | 171.815 | 118.615 | 171.815 | 171.815 | 139.965
| EPF | 12% | 969 | 969 | 969 | 969 | 969 | 969 | 969 | 969 | 969 | 969 | 969 | 969 | 789 | 789 | 969 | 789 | 789 | 669 | 969 | 789 | 969 | 969 | 969 | 969 | 669 | 969 | 969 | 789
SUB TOTAL |  |  | 1212.6187 | 1176.9953 | 1176.9953 | 1176.9953 | 1176.9953 | 1176.9953 | 1176.9953 | 1176.9953 | 1176.9953 | 1176.9953 | 1176.9953 | 1176.9953 | 940.3541 | 975.9775 | 1230.4304 | 958.1658 | 958.1658 | 800.405 | 1212.6187 | 958.1658 | 1140.815 | 1140.815 | 1140.815 | 1140.815 | 787.615 | 1140.815 | 1140.815 | 928.965
Employer | ESI | 4.75% | 661.2508 | 564.5587 | 564.5587 | 564.5587 | 564.5587 | 564.5587 | 564.5587 | 564.5587 | 564.5587 | 564.5587 | 564.5587 | 564.5587 | 410.8182 | 507.5103 | 709.5968 | 459.1642 | 459.1642 | 356.6706 | 661.2508 | 459.1642 | 466.355 | 466.355 | 466.355 | 466.355 | 321.955 | 466.355 | 466.355 | 379.905
| EPF | 13.61% | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 895 | 895 | 1100 | 895 | 895 | 759 | 1100 | 895 | 1100 | 1100 | 1100 | 1100 | 759 | 1100 | 1100 | 895
SUB TOTAL |  |  | 1761.2508 | 1664.5587 | 1664.5587 | 1664.5587 | 1664.5587 | 1664.5587 | 1664.5587 | 1664.5587 | 1664.5587 | 1664.5587 | 1664.5587 | 1664.5587 | 1305.8182 | 1402.5103 | 1809.5968 | 1354.1642 | 1354.1642 | 1115.6706 | 1761.2508 | 1354.1642 | 1566.355 | 1566.355 | 1566.355 | 1566.355 | 1080.955 | 1566.355 | 1566.355 | 1274.905
ADMINISTRATION CHARGES
Bonus |  | 8.33% | 291.55 | 291.55 | 291.55 | 291.55 | 291.55 | 291.55 | 291.55 | 291.55 | 291.55 | 291.55 | 291.55 | 291.55 | 291.55 | 291.55 | 291.55 | 291.55 | 291.55 | 291.55 | 291.55 | 291.55 | 291.55 | 291.55 | 291.55 | 291.55 | 291.55 | 291.55 | 291.55 | 291.55
Leave Component |  | 8.33% | 817.8394 | 817.8394 | 817.8394 | 817.8394 | 817.8394 | 817.8394 | 817.8394 | 817.8394 | 817.8394 | 817.8394 | 817.8394 | 817.8394 | 666.2334 | 666.2334 | 817.8394 | 666.2334 | 666.2334 | 564.6074 | 817.8394 | 666.2334 | 817.8394 | 817.8394 | 817.8394 | 817.8394 | 564.6074 | 817.8394 | 817.8394 | 666.2334
Uniform & Tools |  | (Pro-rata) | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 151 | 152 | 155 | 156 | 158 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
SUB TOTAL |  |  | 1259.3894 | 1259.3894 | 1259.3894 | 1259.3894 | 1259.3894 | 1259.3894 | 1259.3894 | 1259.3894 | 1259.3894 | 1260.3894 | 1261.3894 | 1264.3894 | 1113.7834 | 1115.7834 | 1259.3894 | 1107.7834 | 1107.7834 | 1006.1574 | 1259.3894 | 1107.7834 | 1259.3894 | 1259.3894 | 1259.3894 | 1259.3894 | 1006.1574 | 1259.3894 | 1259.3894 | 1107.7834
INSURANCE
Medical & Accidential Insurance |  |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 101 | 102 | 105 | 106 | 108 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Others
SUB TOTAL |  |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 101 | 102 | 105 | 106 | 108 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
FINAL
Cash In hand |  |  | 13000 | 11000 | 11000 | 11000 | 11000 | 11000 | 11000 | 11000 | 11000 | 11000 | 11000 | 11000 | 8000 | 10000 | 14000 | 9000 | 9000 | 7000 | 13000 | 9000 | 8968.735 | 8968.735 | 8968.735 | 8968.735 | 6281.935 | 8968.735 | 8968.735 | 7360.585
CTC |  |  | 17041.7089 | 14909.3933 | 14909.3933 | 14909.3933 | 14909.3933 | 14909.3933 | 14909.3933 | 14909.3933 | 14909.3933 | 14911.3933 | 14913.3933 | 14919.3933 | 11174.4057 | 13310.7212 | 18107.8666 | 12228.5634 | 12228.5634 | 9730.683 | 17041.7089 | 12228.5634 | 12743.7444 | 12743.7444 | 12743.7444 | 12743.7444 | 8965.1124 | 12743.7444 | 12743.7444 | 10480.6884
SERVICE PROVIDER CHARGES
Service Charges |  | 10% | 1704.1709 | 1490.9393 | 1490.9393 | 1490.9393 | 1490.9393 | 1490.9393 | 1490.9393 | 1490.9393 | 1490.9393 | 1491.1393 | 1491.3393 | 1491.9393 | 1117.4406 | 1331.0721 | 1810.7867 | 1222.8563 | 1222.8563 | 973.0683 | 1704.1709 | 1222.8563 | 1274.3744 | 1274.3744 | 1274.3744 | 1274.3744 | 896.5112 | 1274.3744 | 1274.3744 | 1048.0688
BILL TO CLIENT |  |  | 18746 | 16400 | 16400 | 16400 | 16400 | 16400 | 16400 | 16400 | 16400 | 16403 | 16405 | 16411 | 12292 | 14642 | 19919 | 13451 | 13451 | 10704 | 18746 | 13451 | 14018 | 14018 | 14018 | 14018 | 9862 | 14018 | 14018 | 11529
|  |  | 13000 | 11000 | 11000 | 11000 | 11000 | 11000 | 11000 | 11000 | 11000 | 11000 | 11000 | 11000 | 8000 | 10000 | 12000 | 9000 | 9000 | 7000 | 13000 | 9000 | 13000 | 10000 | 10000 | 12000 | 8000 | 12000 | 11000 | 10000

## HK - Secr Equipments
HOUSEKEEPING EQUIPMENT COST
Sl.No | Name of Machines | Brand | Cost/ unit | Life in months | Common | Total | Total Cost |  | Amortized Cost | INDEX
1 | Walk Behind- Auto Scrubbr/ Dryr | NILFISK | 130000 | 24 | 1 | 1 | 130000 | 5416.6667 | 5416.6667
1 | SINGLE DISC MACHINE | NILFISK | 70000 | 24 | 2 | 2 | 140000 | 2916.6667 | 5833.3333
2 | MANUAL ROAD SWEEPER | COMAC | 15000 | 24 | 1 | 1 | 15000 | 625 | 625
3 | HIGH PRESSURE JET | TASKI | 70000 | 24 | 1 | 1 | 70000 | 2916.6667 | 2916.6667
4 | WET/DRY VACUUM | EUREKA | 20000 | 24 | 2 | 2 | 40000 | 833.3333 | 1666.6667
5 | WRINGER TROLLEY | UNGER | 5000 | 12 | 10 | 10 | 50000 | 416.6667 | 4166.6667
6 | GLASS CLEANING KIT WITH TELESCOPIC POLE | KARAM | 10000 | 12 | 2 | 2 | 20000 | 833.3333 | 1666.6667
7 | CADDY & SIGNAGES | CONTA | 1000 | 12 | 10 | 10 | 10000 | 83.3333 | 833.3333
Sub Total | [6 empty] | 345000 |  | 23125
| SPARES @ 20% | [7 empty] | 4625
| INTEREST @ 12% | [7 empty] | 2775
TOTAL cost per month (b) | [8 empty] | 30525
SECURITY EQUIPMENTR C COSTING
Sr.No | Equipment |  |  | Monthly Rental | Common | Total | Total Rental
1 | DFMD |  |  | 2000 |  | 10 | 20000
2 | HHMD |  |  | 800 |  | 10 | 8000
3 | Wireless Set |  |  | 1000 |  | 15 | 15000
| Under Carrage Mirror |  |  | 250 |  | 2 | 500
| GRAND TOTAL |  |  |  |  | 35 | 43000

## SinkingFundEstimation
Sinking Fund Estimation-
Cost of Equipments | [8 empty] | Actual Cost of Euipment to be considered |  |  |  | # of years in which replacement will be required |  |  |  | % of Replacement required |  |  |  | INDEX
FAS,CCTV,IBMS&PAS | [8 empty] | 2.6742 |  |  |  | 10 |  |  |  | 25%
Chillers | [8 empty] | 1.5695 |  |  |  | 15 |  |  |  | 50%
Package Units | [8 empty] | 3.0892 |  |  |  | 12 |  |  |  | 40%
33KV Transformers | [8 empty] | 0.888 |  |  |  | 20 |  |  |  | 50%
Elevators | [8 empty] | 3.8043 |  |  |  | 12 |  |  |  | 30%
Diesel Generators | [8 empty] | 4.7743 |  |  |  | 15 |  |  |  | 30%
Total Cost taken for refurbishment | [8 empty] | 16.7995 | [7 empty] | 37.5%
Area in sft | 211750
Inflation yoy for Equipment Cost | 4%
Replacement Funds required considering YOY Inflation >> | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
FAS,CCTV,IBMS&PAS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4649
Chillers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4133 | 0 | 0 | 0 | 0 | 0
Package Units | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33KV Transformers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97286
Elevators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diesel Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5795 | 0 | 0 | 0 | 0 | 0
Replacement Funds required >> | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98962 | 0 | 3.8056 | 0 | 0 | 3.9928 | 0 | 0 | 0 | 0 | 2.4377
| 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
Sinking Fund Generation Account | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Interest Rate possible on sinking fund ( post TDS) | 7%
Inflation yoy | 4%
Rate Per sqft paid for Sinking Fund | 1.1566 | 1.2029 | 1.251 | 1.301 | 1.3531 | 1.4072 | 1.4635 | 1.522 | 1.5829 | 1.6462 | 1.712 | 1.7805 | 1.8517 | 1.9258 | 2.0028 | 2.083 | 2.1663 | 2.2529 | 2.343 | 2.4368
Contribution from Annual Sinking Fund | 0.29389 | 0.30565 | 0.31787 | 0.33059 | 0.34381 | 0.35756 | 0.37187 | 0.38674 | 0.40221 | 0.4183 | 0.43503 | 0.45243 | 0.47053 | 0.48935 | 0.50892 | 0.52928 | 0.55045 | 0.57247 | 0.59537 | 0.61918
Carry Forward from previous Year | 0 | 0.31446 | 0.66352 | 1.0501 | 1.4773 | 1.9486 | 2.4676 | 3.0382 | 3.6647 | 4.3516 | 4.1142 | 4.8677 | 1.8869 | 2.5224 | 3.2226 | 0 | 0.56633 | 1.195 | 1.8911 | 2.6606
Total Amount on which interest is applicable | 0.29389 | 0.62011 | 0.98139 | 1.3807 | 1.8211 | 2.3062 | 2.8395 | 3.425 | 4.0669 | 4.7699 | 4.5492 | 5.3201 | 2.3574 | 3.0118 | 3.7315 | 0.52928 | 1.1168 | 1.7674 | 2.4865 | 3.2798
Interest Generated Annual | 0.020572 | 0.043408 | 0.068697 | 0.096647 | 0.12748 | 0.16143 | 0.19876 | 0.23975 | 0.28469 | 0.33389 | 0.31845 | 0.37241 | 0.16502 | 0.21083 | 0.26121 | 0.03705 | 0.078175 | 0.12372 | 0.17406 | 0.22958
End of Year Amount | 0.31446 | 0.66352 | 1.0501 | 1.4773 | 1.9486 | 2.4676 | 3.0382 | 3.6647 | 4.3516 | 5.1038 | 4.8677 | 5.6925 | 2.5224 | 3.2226 | 3.9928 | 0.56633 | 1.195 | 1.8911 | 2.6606 | 3.5093
Sinking Fund Account Usage | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Starting Balance | 0.31446 | 0.66352 | 1.0501 | 1.4773 | 1.9486 | 2.4676 | 3.0382 | 3.6647 | 4.3516 | 5.1038 | 4.8677 | 5.6925 | 2.5224 | 3.2226 | 3.9928 | 0.56633 | 1.195 | 1.8911 | 2.6606 | 3.5093
Sinking Fund Consumed | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98962 | 0 | 3.8056 | 0 | 0 | 3.9928 | 0 | 0 | 0 | 0 | 2.4377
Ending Balance | 0.31446 | 0.66352 | 1.0501 | 1.4773 | 1.9486 | 2.4676 | 3.0382 | 3.6647 | 4.3516 | 4.1142 | 4.8677 | 1.8869 | 2.5224 | 3.2226 | 0 | 0.56633 | 1.195 | 1.8911 | 2.6606 | 1.0716
Maximum Outage | 0