# Minutes of Meeting-MIS Review

# Ref No: 007/Conference room/XXXX-Corporate office/21.12.2023

Attendees:

- X – Chief Engineer/ Emerzhent

- Y – Property Manager (OW &TD)

- Z – Property Manager (SLNT)

- W – General Manager Corporate

- V - DGM Procurement & Projects

- U– Chief Operating Officer

- T

| Sl no | Site | Topic | Description | Remarks |
| --- | --- | --- | --- | --- |
| 1 | All sites | Vendor Performance Score card | Mr. Dhanunjay enquired, how the vendors performance has been rated at all the sites managed by EPMS | Mr. Kiran Conveyed that, vendor performance score card was implemented at SLN Terminus and the same would be replicated and maintained at all sites, however we are checking the possibilities of incorporation of the same with the eFacility application |
| 2 | All sites | Man power revision in the Budget | Mr. Dhanunjay asked to freeze the existing Manpower deployment at ONE WEST, if there is no such additional deployment as of now. | Mr.Siva conveyed that, this will be updated in the coming year budget for all the sites. |
| 3 | Onewest & The District | Sinking fund provision in Onewest | while explaining about the DG Alternator failure at ONEWEST, had a discussion on over usage of Elevators and critical equipment pertaining to ADP operations. | Mr.Dhanunjay insisted on the provision of sinking fund in ONE WEST budget , because of the concerns on the over usage of elevators and critical equipment |
| 4 | The District | Transformer shed | EPMS requested a Shed over the outdoor transformers to avoid failures from weather conditions and Rain. At present both the transformers bus ducts failed because of moisture. | Mr.Dhanunjay asked us to submit list of critical works along with impact of the same to take further approvals. |
| 5 | The District | Gaps to be sealed in between floor-to-floor Shafts | to avoid Pest movement from floor-to-floor EPMS requested ceiling gaps closure | Mr.Dhanunjay asked us to submit list of critical works along with impact of the same to take further approvals. |
| 6 | The District | Drain line & Concrete work for levelling the floor at external peripheral area | Provision for Water discharge, generated from STP \ WTP and rain water | Mr.Dhanunjay asked Mr.Rajavaradhan to co-ordinate with Mr.Phani regarding approvals from Govt. Authorities |
| 7 | The District | STP Non-operational | During discussion on the STP Issues regarding the entry of Oil and Grease in to the STP, EPMS requested Oil and Grease trap installation at Basement level . Which is costing us around INR 7 Lakhs. | Mr. Dhanunjay approved for the installation of the Oil and grease Trap. He instructed EPMS to try and collect the amount from respective tenants by sending a notice to them. |
| 8 | ONEWEST | De-watering drain line | Provision for Water discharge, generated from STP \ WTP and rain water | Mr.Dhanunjay asked Mr.Rajavaradhan to co-ordinate with Mr.Phani regarding approvals from Govt. Authorities |
| 9 | ONEWEST | Basement flooring rectification | Drive way flooring damaged in the basements. ADP insisting on the rectification of the same. | Mr.Dhanunjay asked us to submit list of critical works along with impact of the same to take further approvals. |
| 10 | ONEWEST | Lift Shaft Air-Conditioning | Observed increase in temperatures in Elevator drives, which is effecting elevator movement for 30 to 40 sec Approximately. simultaneously all the previous calls were cancelled this is effecting ADP Employees moment. Predicted it will be more problematic in summer due to rise in temperature | Mr.Dhanunjay asked us to submit list of critical works along with impact of the same to take further approvals. |
| 11 | ONEWEST | Nagoor-ji Stack parking | Vendor is out of reach and non-responsive - few works still pending and previous installation were damaged and unable to utilize | Mr.Dhanunjay asked Mr.Rajavaradhan to contact with the vendor through Email |
| 12 | SLN Terminus | Solar-Metering | Mr.Dhanunjay asked about clarification on the Solar metering. | Clarification from Kiran- It’s a stand-alone system and invertor is part of package |
| 13 | SLN Terminus | Renovation plan priority wise | Mr.Dhanunjay asked to prepare costing on the list of works submitted |  |